# GENERAL

## RELATED DOCUMENTS

### Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 specification sections, apply to work of this Section.

### This section is a Division 26 "Basic Materials and Methods" section, and is a part of each Division 16 26 section making reference to wiring devices specified herein.

## DESCRIPTION OF WORK

### The extent of wiring device work is indicated by drawings and schedules. Wiring devices are defined as single discrete units of electrical distribution systems which are intended to carry, but not utilize electrical energy.

### NOTE TO SPECIFIER:  REVISE LIST OF WIRING DEVICES ACCORDING TO SPECIFIC PROJECT REQUIREMENTS.

### Types of electrical wiring devices in this Section include the following:

#### Receptacles

#### Switches

#### Wall Plates

#### Dimmer Controls

#### Floor Outlets

#### Underfloor Duct and Fittings

## QUALITY ASSURANCE

### Manufacturers:  Firms regularly engaged in manufacture of wiring devices of types, sizes, and ratings required, whose products have been in satisfactory use in similar service for not less thean 3 years.

### Installer:  Qualified with at least 2 years of successful installation experience on projects with electrical installation work similar to that required for this project.

## REFERENCES

### NEC Compliance:  Comply with NEC as applicable to construction and installation of electrical wiring devices.

### UL Compliance and Labeling:  Provide electrical wiring devices which have been UL listed and labeled.

### NEMA Compliance:  Comply with NEMA standards for general and specific purpose wiring devices.

### NECA Compliance:  Comply with NECA's "Standard of Installation."

  - SUBMITTALS

### Product Data:  Submit manufacturer's data on electrical wiring devices.

# PRODUCTS

NOTE TO SPECIFIER:  REVISE LIST OF MANUFACTURERS AS REQUIRED FOR THE PROJECT.

## Manufacturers:  Subject to compliance with requirements, provide products of one of the following:

### Pass and Seymour (P&S) Corporation

### Cooper

### Hubbell, Inc.

### Leviton, Inc.

### Crouse Hinds

### Wiremold

### Lutron

### Walker Duct

### Cellco

### Lutron

## LIGHT SWITCHES WIRING DEVICES

### General:  Where shown on the drawings, furnish and install wiring devices light switches indicated by the appropriate symbols. Unless noted otherwise, all light switches shall be rated for “extra heavy-duty use” or “industrial use” as applicable by manufacturer descriptions. Wiring devices shall be products of Pass and Seymour Corporation, or equal. Catalog numbers shown below are P & S hard use specification grade. Similar devices manufactured by Others Hubbell or Leviton shall be equally acceptable.

### Low voltage, digital light switches are not specified in this document. It is expected such devices are provided with digital lighting control package included with the project, where applicable. Digital lighting controls shall be manufactured by the same company that makes the digital lighting control system in use or being proposed for the project.

### Manual Switches:  Catalog numbers shown below are based on P & S industrial, heavy-duty grade devices. Equal products will be accepted. Branch circuit switches shall be flush tumbler (rocker) type as follows:

#### Single Pole					20AC1 Series - Gray

#### Two Pole					20AC2 Series - Gray

#### Three-Way					20AC3 Series - Gray

#### Four-Way					20AC4 Series - Gray

#### Single Pole SW With Pilot 			20-AC1-RPL Series

#### Switches for normal systems shall be gray, unless otherwise required by Architect.

#### Switches for emergency systems shall be as shown above, but red in color.

### Motion Sensing Switches: Catalog numbers shown below are based on Lutron devices. Equal products will be accepted. Provide different switch technologies as follows:

#### Wall Mounted Line Voltage Dual Technology PIR type Occupancy Sensing Switches: Watt Stopper type WA-200 Lutron MS-A102 – 120/277 – Ivory. with time delay set at 15 minutes. Features ‘vacancy’ and ‘occupancy’ operation modes, tamper resistant PIR lens, 900 sq. ft. (major motion) and 400 sq ft. (minor motion) coverage zones, nominal. Minimum load capacity of 6 amps of lighting load, 120-277V, no neutral wire required, with adjustable (5-30 min) timeout. Set for 15 min. timeout & vacancy mode, unless otherwise noted. Units using power pack are discouraged but where required mount power pack above accessible ceiling and provide all necessary wiring between switch and power pack.

#### Ceiling Mounted Line Voltage Dual Technology Ultrasonic Occupancy Sensing Switches: Watt Stopper type WT-1105 Lutron LOS-CDT Series – 120/277 - Ivory. with time delay set at 15 minutes with a Watt Stopper B120E-P power pack. From 500 sq. ft. (180 deg field of view) to 2000 sq. ft. (360 deg field of view) coverage zones. Features threshold sensitivity adjustment, LED motion indicator, airflow compensation, and timer adjustments. Mounts available for suspended ceilings, drywall ceilings, and suspended (no ceiling) applications. Mount power pack above accessible ceiling. Provide all necessary wiring between power pack and occupancy sensor.

#### Wall Mounted Line Voltage Dual Technology Occupancy Sensing Switches: Watt Stopper type DT-200 – Ivory with time delay set at 15 minutes with a Watt Stopper B120E-P power pack. Mount power pack above the accessible ceiling. Provide all necessary wiring between power pack and occupancy sensor.

### Dimmer Switches:  Provide dimmer switches according to the following (all catalog numbers are Lutron Nova T series, unless otherwise noted).  At minimum, all dimmer switches shall be rated to accommodate the load shown to be switched on the Drawings. All dimmers shall be LED rated.

Incandescent Dimmers	Catalog No.

120A Volt, 600 Watt, Single Pole	NT-600

120 Volt, 1000 Watt, Single Pole	NT-1000

120 Volt, 1500 Watt, Single Pole	NT-1500

120 Volt, 2000 Watt, Single Pole	NT-2000

Incandescent Low Voltage

Dimmers (for transformer

supplied low voltage lamps)

120 Volt, 600 VA (500W), Single Pole	NTLV-600

120 Volt, 1000 VA (800W), Single Pole	NTLV-1000

120 Volt, 1500 VA (1200W), Single Pole	NTLV-1500

Fluorescent Dimmers (for 30 &

40W rapid start lamps with

magnetic dimming type ballasts)

120 Volt, 1 to 10 Lamps, Single Pole	NF-10

120 Volt, 6 to 20 Lamps, Single Pole	NF-20

120 Volt, 14 to 30 Lamps, Single Pole	NF-30

277 Volt, 1 to 12 Lamps, Single Pole	NF-10-277

277 Volt, 6 to 24 Lamps, Single Pole	NF-20-277

## RECEPTACLES

NOTE TO SPECIFIER:  RECEPTACLES ARE FIGURE 8 TYPE-CHANGE COLOR AS DESIRED. FOR HARD USE SPECIFICATION GRADE USE 26352 FOR RECTANGULAR TYPE AND 5352 FOR FIGURE 8 TYPE.

### All receptacles shall be side and back wired, self-grounding of the type indicated on the drawings, or as follows. Catalog numbers shown below are Pass & Seymour specification grade unless otherwise indicated.  Similar devices manufactured by Hubbell or Leviton shall be equally acceptable: Unless noted otherwise, all receptacles shall be UL listed ‘Federal’ grade (UL 498) and rated for “extra heavy-duty use” or “industrial use” as applicable by manufacturer descriptions. Catalog numbers shown below are based on Leviton industrial, heavy-duty grade devices. Equal products will be accepted.  Receptacles shall be gray unless project specifications differ:

      - Duplex Convenience Receptacles		5362 Series-Gray

20A-125V (Grounding Type)

      - Weatherproof Duplex Receptacles		5362 WP Series-Gray  with

20A-125V (Grounding Type)		Weatherproof F.S. Plate

      - Duplex GFI Receptacle	5362 Series with indicator light 2091-Gray

20A-125V

      - Weatherproof Duplex	5362 Series with indicator light and  2091 with 4511 (horizontal) or

GFI Receptacle 20A-125 Volt		4512 (vertical) wWeatherproof wWall pPlate

      - Clock Hanger Outlet	S3733-SS

      - Hospital Grade Receptacle  	5362 Series 8300 Gray for Normal Power and

20A-125 Volt 			8300 Red for Emergency Power

      - Hospital Grade GFI Receptacle  	5362 Series 2091-HG Gray for Normal Power and

20A-125 Volt 			2091-HG Red for Emergency Power

      - Safety Receptacle	SG-62H Gray for Normal and

SG-62H Red for Emergency

      - Emergency Duplex Receptacle	5362 Series 8300 Red

20 Amp, 125 Volt

      - Isolated Ground Receptacles 	5362 Series IG6300 with Orange Cover Plate

20A-125 Volt, Ground Wire shall be

routed back to main switchboard ground

or separately derived system ground in

accordance with NEC requirementsNOTE TO SPECIFIER:  REVISE THE FOLLOWING PARAGRAPH TO ASSURE THAT ALL OF THE AREAS THAT NEED TO HAVE HOSPITAL GRADE RECEPTACLES ARE LISTED.

      - USB Receptacles 	M58AA Series

20A-125 Volt

    - Receptacles on emergency power shall be red in color. Cover plates for emergency outlets in these areas shall be engraved with panel and circuit no. designation per NEC. Engraving shall be 1/8" high, block style letters, with red filler on front side of cover plates.

## PLATES

NOTE TO SPECIFIER:  CHECK PLATE FINISH WITH ARCHITECT AND CHOOSE ONE OF THE TWO PARAGRAPHS BELOW OR REVISE ACCORDINGLY.  COORDINATE COLOR WITH ARCHITECT AND INTERIOR DESIGNER.

### Furnish and install wall plates for all wiring devices.  Plates for flush devices shall be Pass and Seymour "RP" Series high impact thermoplastic or equal. , and shall be gray in color.  Oversize plates are not acceptable.  Weatherproof switch plates shall be Crouse Hinds DS185 type or equal.  Where switches and/or receptacles are shown adjacent to each other, provide a common cover plate for each group of devices.

OR

### Furnish and install wall plates for all wiring devices.  Plates shall be Pass and Seymour Type 302 stainless steel or equal. Oversize plates are not acceptable. Weatherproof switch plates shall be Crouse Hinds DS185 type or equal. Where switches and or receptacles are shown adjacent to each other, provide common plate for each group of devices.

## MULTI-OUTLET SURFACE ASSEMBLIES

NOTE TO SPECIFIER:  REVISE OR DELETE PARAGRAPH 2.5.1 AS REQUIRED.  DELETE THIS PARGRAPHS IF MULTI-OUTLET SURFACE ASSEMBLIES OR POWER POLES ARE SPECIFIED ON THE DRAWINGS.

### Provide two piece surface metal raceway assemblies manufactured by the Wiremold Company or Walker Parkersburg Products, complete including fittings, devices, end closures, conduit entrance fittings, elbows, and boxes.  Except where specified otherwise on the drawings, provide Wiremold G-4000 Series or equal base cover and divider and provide accessory devices as noted on the drawings.

## FLOOR OUTLETS

NOTE TO SPECIFIER:  REVISE OR DELETE PARAGRAPHS 2.7.1 & 2.7.2 AS REQUIRED.  DELETE THESE PARAGRAPHS IF THESE DEVICES ARE SPECIFIED ON THE DRAWINGS.

### Flush Mounted Floor Boxes and Floor Outlets:  Provide Steel City or equal No. 664 box, No. 664-CST cover, one 20A, 125V duplex receptacle, one 664RP receptacle faceplate, and one 664BP blank faceplate for each flush mounted floor convenience outlet.  When carpet is indicated on the finish schedule, supply each floor box or outlet with an appropriate carpet flange.

### Poke-Thru Service Fittings:  Provide Steel City poke-thru service fittings or approved equal complete with a FPT-400 series or equal fire rated insert suitable for the distribution of power, communications, and data wiring.  Provide FPT-400 series or equal service fitting heads with faceplate types as noted on the drawings, or as required to meet specified project needs.

NOTE TO SPECIFIER:  REVISE OR DELETE PARAGRAPHS ON UNDERFLOOR DUCTS AND FITTINGS AS REQUIRED.

## UNDERFLOOR DUCT AND FITTINGS

### This Contractor shall furnish and install an underfloor duct system as shown on the plans, complete with all junction boxes, end caps, elbows, conduit adapters, supports, anchors, covers, flanges and other necessary components for a complete and workable installation.

### The system shall consist of No. 2 power duct and No. 4 communications duct with inserts 24" on center.  Duct shall be manufactured by Walker/Parkersburg, Cellco or approved equal.

### Power duct and comm./computer duct shall be aligned with 1-inch spacing between parallel duct runs using duct supports spaced at 5 foot intervals and as recommended by the manufacturer.  Top of inserts shall be made watertight with sealing compound.

### Provide service fittings where shown on the plans.  Prior to installation verify service fitting locations with the Owner.

### Devices and cover plates shall be similar to those specified for floor outlets.

## Where devices are installed on exposed fittings or boxes, the plates shall be galvanized and of a type designed to fit the box.  Blank covers shall be installed on all boxes without devices or fixtures, of same type as installed on devices in the room or area.

## Test wiring devices to ensure electrical continuity of grounding connections and proper polarity.

# EXECUTION

## INSTALLATION

### Install wiring devices as indicated in compliance with manufacturer's written instructions, applicable requirements of the NEC and NECA's "Standard of Installation," and in accordance with recognized industry practices to fulfill project requirements.

### Coordinate with other work including painting, electrical boxes and wiring work, as necessary to interface installation of wiring devices and other work.

### Testing:  Test wiring devices for electrical continuity and proper polarity of connections.  Test wiring devices to demonstrate compliance with requirements.

### All devices outlets shall be located as shown on the drawings, except that where practicable, outlets shall be located in center of panels or trim or otherwise symmetrically located to conform with existing structural layout.  Outlets incorrectly installed shall be corrected.  Damaged items or damaged finishes shall be repaired or replaced at no expense to the Owner.

### Devices Outlets shall be set plumb or horizontal and shall extend to the finished surface of the walls, ceiling or floor, as the case may be, without projecting beyond the same.

### Devices Receptacles, switches, etc., shown on wood trim, cases or other fixtures shall be installed symmetrically; and, where necessary, shall be set with the long dimensions of the plate horizontal, or ganged in tandem.

### Where dimmer switches are shown adjacent to standard switches, both shall be installed in separate back boxes with adequate space between so that neither cover plate requires cutting.

### Where devices are shown near wall openings, coordinate location if corner guards are to be installed so that cover plates do not require cutting.

### Where devices are shown mounted adjacent to one another on the drawings, provide multi-gang faceplates to cover all devices.

### Where devices are shown mounted back-to-back in a wall, stagger locations to avoid sound and air migration between the spaces. Do not mount devices directly back-to-back with each other.

### Where devices are provided in ‘clean room’ type spaces, provide inserts within receptacles to minimize air flow through receptacle interior cavity into the space.

END OF SECTION 262726