Computer Aided Drafting (CAD) Standards

Facilities Planning and Construction

2013

Table of Contents

1	Introduction	3

1.1	The Need for (CAD) Standards	3

1.2	Vendor Expectations	3

1.3	Building Information Modeling (BIM)	4

1.4	Standard of Production	4

2	CAD Drawing Setup Process	5

2.1	CAD Drawing File Format	5

2.1.1	Electronic File Media	5

2.2	Sheet Numbering and Drawing File Identification	5

2.2.1	Sheet Numbering	5

2.2.2	Drawing File Naming	5

2.2.3	Alternate File Naming	6

2.3	Drawing Environment	6

2.3.1	External Reference & Imported Image Files	6

2.3.2	Model Space and Paper Space	7

3	CAD Parameters	8

3.1	Units and Tolerances	8

3.1.1	Units of Measure	8

3.1.2	Tolerances	8

3.1.3	Scale Factors	8

3.1.4	Scale Factor and Text Table	8

3.2	Drawing	9

3.3	Text	9

3.3.1	Text Descriptions	9

3.3.2	Text Style, Font and Size Table	10

3.4	Dimensioning	11

3.4.1	Dimension Description	11

3.4.2	Dimension Style Parameters	11

3.5	Blocks, Details and Title Blocks	12

3.5.1	Block Definitions	12

3.5.2	UNL FPC Defined Blocks and Details	13

3.5.3	Vendor Defined Blocks and Symbols	13

3.5.4	UNL Title Blocks	13

3.5.5	UNL North Arrow	14

3.5.6	Addenda, Revisions	14

3.6	Layers	14

3.6.1	Layer Description	14

3.6.2	AIA CAD Layer Naming Summary	15

3.6.3	UNL FPC Layer Properties	18

3.6.4	UNL FPC Layer Property Table	18

3.6.5	Layer Attributes	24

3.6.6	Layer Colors	24

3.6.7	Layer Linetypes	25

3.6.8	Layer Lineweight	25

4	CAD Templates	25

4.1	Text, Notes, Fonts Hyperlink	25

4.2	Dimension Style Hyperlink	25

4.3	Blocks, Details Hyperlink	25

4.4	Title Blocks, Sheet Sizes, Sheet Titles Hyperlink	25

4.5	Standard UNL Layers Hyperlink	25

4.6	Drawing Templates Hyperlink	25

4.7	Plot Styles Hyperlink	25

5	UNL Space & Planning Requirements	25

5.1	Room Numbering	25

5.2	Door Numbers	26

5.3	Room and Space Area	26

6	CAD Reproduction	26

6.1	UNL Drawing File Disclaimer	26

6.2	Plot Styles	26

6.3	UNL FPC Color and Line Weights	26

6.4	Printing	27

6.5	Sheet Size	28

6.6	Delivery	28

6.7	Reproduction Quality Assurance	29

7	CAD Project Closeout Documentation	30

7.1	Reference Binding	30

7.2	Conversions and CAD Translations	30

7.3	As-Built Documents	30

7.4	Construction Revisions	31

7.5	Delivery	31

7.6	Waiver Procedure	31

# Introduction

## The Need for (CAD) Standards

The University of Nebraska–Lincoln Facilities Planning and Construction Department (UNL FPC) is responsible for archiving electronic “as-built” construction documents produced as part of capital construction projects.

UNL FPC is also is responsible for generating and maintaining accurate electronic floor plans for all campus facilities.  These floor plans support many campus entities and initiatives including telecommunications, building automation systems, CCTV, access control, maintenance management, security, Institutional Research & Planning (IRP) and Geographic Information Systems (GIS).

In addition, UNL FPC staff performs Architectural/Engineering design services on an in-house basis for some capital construction projects.

In order to support UNL FPC’s missions, a well-defined and detailed set of Computer Aided Design (CAD) standards are required in order to maximize efficiencies and usability.

This document details UNL FPC’s CAD standards for the production and delivery of CAD documents for all capital construction projects.

## Vendor Expectations

UNL FPC require that all outside vendors submit the most current version of Autodesk AutoCAD®.dwg formatted CAD files that are fully compliant with all of the standards outlined herein.  This includes all capital construction design submittals and final “as-built” documents.

All files submitted should have no significant loss of drawing entities or project data that can result from standard CAD file translation procedures.  PDF and DXF files will not be accepted at project closeout as a substitution for “.dwg” CAD file deliverables.

## Building Information Modeling (BIM)

The University recognizes the benefits of BIM software but has not fully developed a well-defined set of standards for deliverables that make use of this technology.  As this technology continues to evolve, UNL FPC will review and expand these CAD Standards to include BIM software standards in order to ensure the same consistency with models.  It shall be known, at this time, when BIM models are used as part of the design process then the model shall be converted/exported to AutoCAD®.dwg formatted CAD files that are fully compliant with all of the standards outlined herein.

## Standard of Production

The intent for the standard production of drawings and plans is to allow a multitude of personnel to review, revise, share, maintain and print various archived projects which all have similar parameters.  These parameters include:

- Layering and colors

- Scale factors, line types and line weights

- Font type and size

- Room and door numbering

- Title block and sheet titles

- Drawing sequence and sheet numbers

- Model/Paper space and external reference files (Xrefs)

UNL FPC has adopted the latest version of the AIA CAD Guidelines found in the United States National CAD Standard.  All layer names and descriptions shall follow these standards.  Some layer attributes in the AIA CAD Guidelines have been predefined by UNL FPC with set Colors, Linetypes and specific layer names in order to maximize the printed clarity of archived drawings and to conform to core layer line weight/color assignments.  It is required that all vendors providing CAD documents to the University adopt the AIA CAD Guidelines as well as implement UNL FPC’s strict predefined layer attributes described herein.

# CAD Drawing Setup Process

## CAD Drawing File Format

### Electronic File Media

UNL FPC require that vendors submit AutoCAD®.dwg formatted CAD files for all capital construction intermediate design submittals and final “as-built” documents that are fully compliant with all of the standards outlined herein, and which have no significant loss of drawing entities or project data that can result from standard CAD file translation procedures.  PDF and DXF files will not be accepted at project closeout as a substitution for “.dwg” CAD file deliverables only as supplemental information.

All CAD files submitted shall be in the latest addition of Autodesk AutoCAD®.dwg format.

## Sheet Numbering and Drawing File Identification

### Sheet Numbering

UNL FPC requires that all drawing file names and drawing sheet numbers follow the format set herein.  The drawing/project sheet number for all projects must follow the single or double discipline, uppercase alphabetic designator followed by a three digit numerical sheet number with a dot, no spaces.  The three digit numerical number and dot can be used in any fashion at the discretion of the coordinating professional and shall be similarly repeated by all disciplines.  The numbers shall be arranged and used on a project by project basis as it pertains to the size and complexity of a project, the number of floors, construction phases, etc.  A single or double digit number or sheet number not using a dot is unacceptable (i.e. A100, E100).  A building name, acronym, project title or progress phase shall not be included in any way as part of the sheet numbering.  Below is an example of the UNL FPC sheet numbering nomenclature required:

“G0.01” or “A1.00” or “MD2.10” or “FP3.30”, etc.

The first digit represents the discipline designator (G – General Sheet) (A – Architectural Sheets) (MD – Mechanical Demolition Sheets) (FP – Fire Protection Sheets) etc.  Followed by a three digit numerical sheet number with a dot, no spaces (0.01) (1.00) (2.10) (3.30) etc. which is determined by the coordinating professional based on the project complexity/parameters and similarly followed by all other disciplines.

### Drawing File Naming

The drawing/project file name for all projects must be represented with the UNL project number and drawing/project sheet number.  Each CAD, PDF or Revit drawing file shall be preceded with the UNL project number followed by a hyphen and then the drawing sheet number as described herein, above paragraph with no spaces.  Finally, a last dot and then the file extension shall conclude the complete file naming.  A building name, acronym, project title or progress phase shall not be included in any way as part of the file naming.  Below is an example of the UNL FPC file naming nomenclature:

“467123-A1.01.dwg” or “467123-SD2.01.pdf”

The first digits represent the UNL project number (467123), then the hyphen as a placeholder to help make the name more readable and easier to manage, followed by the sheet number (A1.01) (SD2.01).  The sheet number includes the discipline designator (A – Architectural) in this case a single digit used for Architectural but expandable up to two alphabetical characters as indicated for (SD – Structural Demolition).  Next a three digit numerical sheet number with a dot, no spaces and finally the dot file name extension (.dwg – AutoCAD® file) (.pdf – Adobe System File).

### Alternate File Naming

In some cases grouped PDF files, external CAD references/images, zipped files or Revit models may require an alternate nomenclature.  Each PDF, CAD, ZIP or Revit drawing file shall be preceded with the UNL project number followed by a hyphen, then must follow the single or double discipline, uppercase alphabetic designator as deemed appropriate followed by a dot and the grouped file name, external CAD reference description or short Revit Model description, no spaces.  A building name, acronym, project title or progress phase shall not be included in any way as part of the file naming.  Variations of acceptable file naming nomenclature for these types of files are indicated below:

“467123-AE.binder.pdf” or “467123-ME.binder.pdf” or “467123-X.firstfloor.dwg” or                         “467123-A.binder.zip” or “467123-AE.model.rvt”

The first digits represent the UNL project number (467123), then the hyphen as a placeholder to help make the name more readable and easier to manage, followed by the file name (AE.binder) (ME.binder) (X.firstfloor) (A.binder) (AE.model).  The file name includes a single or double digit discipline designator as deemed appropriate (AE = all Arch/Eng. sheets in one file) (ME = Mechanical Electrical sheets) (X = AutoCAD® external reference file) (A = Architectural sheets). Finally the dot and a file name extension (.pdf – Adobe System file) (.dwg – AutoCAD® file) (.zip – Zipped file) (.rvt – Revit file).

## Drawing Environment

### External Reference & Imported Image Files

All drawing floor plans shall be set up for shared use with external reference files (xrefs).  Xrefs must be inserted into sheet files as an attachment or overlay using relative path method in lieu of the full path method.  Relative path allows drawings to be moved from file to file and still maintain their xref links.  Full path (absolute) xref’s are not allowed and should not be used.  UNL FPC encourages that any imported image files such as JPG’s, Tiff’s, BMP’s, PDF’s, etc. used within a CAD drawing also be imported in the same manner and with the same requirements as drawing xrefs.

The base point for all drawing floor plans shall be set in model space at 0,0,0 reference point.  Likewise, all drawing floor plan xrefs inserted into a drawing shall be set in model space at 0,0,0 reference point.  This helps to provide for a consistent insertion placement point from file to file.

Sheet title blocks shall be inserted as an xref into paper space at 0,0,0 reference point.  Title block sheet identification names and sheet page numbers shall not be part of the xref and shall be editable from sheet to sheet.  Title block sheet project information text shall be part of the xref and shall not be editable from sheet to sheet.  UNL FPC requires that all vendors utilize the standard University of Nebraska–Lincoln title blocks available for download at the UNL FPC Design Guideline website.  Refer to Blocks, Details and Title Blocks section herein for additional information.

It shall be known that at project completion, UNL FPC will not accept the submission of any CAD drawings that contain external reference files.  Upon project completion and prior to delivery to UNL FPC all external reference files that were used during CAD production shall be bound, inserted and retained as a block within a single drawing file, this includes the title block and any image files.

### Model Space and Paper Space

UNL FPC requires that all submitted CAD file drawings contain only one variation of the floor plan and site plan in model space. Multiple enlarged partial plans, sections, elevations, details, schedules, dimensions, notes and other material directly related to the drawing set shall also be completed in model space.  Model space shall not contain any alternate design considerations, collaboration ideas, multiple variations of design and other work that is not needed or not meant to be submitted as part of the construction documentation.

Paper is space is reserved to be used for viewports, title block and sheet titling information only.  Multiple paper space tab views, each with its own set of viewports, title block and sheet titling information is acceptable.  Each tab view shall be named with the exact respective individual sheet number of depicted sheet.  Tab view number and respective sheet number shall strictly follow UNL FPC sheet numbering nomenclature set forth herein.

Each paper space tab view in a single drawing file is reserved for viewports depicting the elements of that particular floor, space or area.  Multiple floor plan levels, (i.e. basement, first floor, second floor, etc.) shall be laid out and provided in separate drawing files.  UNL FPC will not accept multiple floor levels within one single drawing file.  Limit paper space layouts to only those sheets being submitted as part of the construction documentation.

# CAD Parameters

## Units and Tolerances

### Units of Measure

All CAD drawings shall be drawn in architectural units of feet and inches with a precision not less than 1/64”.  The format, precision and other conventions to be used in displaying coordinates, distances and angles are set and saved in the drawing units.  This system of measure also pertains to the drawing geometry and appropriate distance values required when dimensioning.

### Tolerances

UNL FPC requires that building floor plans, elevations, details and sections be viewed at not less than 1/16” = 1’-0” scale and no more than 1/2” = 1’-0” drawings scale.  Enlarged partial floor plans, sections and details shall be viewed at not less than 1/4" = 1’-0” and no more than 3/4" = 1’-0” drawing scale.  In some cases certain details, schedules and risers are acceptable to be viewed with no particular drawing scale.  In these instances the text height of non-scaled entities shall follow the guidelines set forth in the text styles, heights and fonts sections.  When circumstances warrant the use of alternate desired drawing scales the vendor shall request a variance through the UNL FPC Project Manager or representative prior to design.

### Scale Factors

All CAD model space drawings shall be drawn at full scale.  For example when drawing a door in CAD, the door should be drawn 3 feet wide and 7 feet tall.

Model space layouts shall be inserted into paper space via viewports as described above herein.  Viewports within paper space are required to be scaled to fit the actual sheet size.  To do this, a scale factor is required so that the final printed or viewed drawing sheet has a usable scale reference. Below is a quick reference guide for standard architectural scale factors to be used in scaling up or down and as a reference for text size associated with the respective scale of the drawing or viewport.

### Scale Factor and Text Table

| Drawing Scale | Scale Factor Up | Scale Factor Down | Viewport Scale | Decimal Scale | Model Space Text Height | Paper Space Text Height |
| --- | --- | --- | --- | --- | --- | --- |
| 1/16" = 1'-0" | 192 | 0.0052083 | 1/192xp | .0625" = 1'-0" | 18” | 3/32” |
| 3/32" = 1'-0" | 128 | 0.0078125 | 1/128xp | .09375" = 1'-0" | 12” | 3/32” |
| 1/8" = 1'-0" | 96 | 0.0104166 | 1/96xp | .125" = 1'-0" | 9” | 3/32” |
| 3/16" = 1'-0" | 64 | 0.015625 | 1/64xp | .1875" = 1'-0" | 6” | 3/32” |
| 1/4" = 1'-0" | 48 | 0.0208333 | 1/48xp | .25" = 1'-0" | 4.5” | 3/32” |
| 3/8" = 1'-0" | 32 | 0.03125 | 1/32xp | .375" = 1'-0" | 3” | 3/32” |
| 1/2" = 1'-0" | 24 | 0.041666 | 1/24xp | .50" = 1'-0" | 2.25” | 3/32” |
| 3/4" = 1'-0" | 16 | 0.0625 | 1/16xp | .75" = 1'-0" | 1.5” | 3/32” |
| 1" = 1'-0" | 12 | 0.08333 | 1/12xp | 1" = 1'-0" | 1.125” | 3/32” |
| 1 1/2" = 1'-0" | 8 | 0.125 | 1/8xp | 1.5" = 1'-0" | 0.75” | 3/32” |
| 3" = 1'-0" | 4 | 0.25 | 1/4xp | 3" = 1'-0" | 0.375” | 3/32” |
| 1” = 10’ | 120 | .00833 | 1/120xp | 1” = 10’ | 11.3 | 3/32” |
| 1” = 20’ | 240 | .00417 | 1/240xp | 1” = 20’ | 22.5 | 3/32” |
| 1” = 30’ | 360 | .00278 | 1/360xp | 1” = 30’ | 33.8 | 3/32” |
| 1” = 40’ | 480 | .00208 | 1/480xp | 1” = 40’ | 45 | 3/32” |
| 1” = 50’ | 600 | .00167 | 1/600xp | 1” = 50’ | 56 | 3/32” |
| 1” = 60’ | 720 | .00139 | 1/720xp | 1” = 60’ | 68 | 3/32” |
| 1” = 100’ | 1200 | .00083 | 1/1200xp | 1” = 100’ | 113 | 3/32” |
| All general drawing plan text size shall print out with a minimum height of 3/32” |  |  |  |  |  |  |

## Drawing

All drawing plan layout entities including but not limited to details, diagrams, hatch patterns, wall types, symbols, line types, text and other predefined entities are strictly required to be created in the correct UNL FPC standard layers as set forth herein and with bylayer properties.  All predefined entities shall revert to layer 0 or bylayer properties when exploded. All predefined entities created in programs other than AutoCAD® shall also revert to bylayer properties.  UNL FPC requires the use of bylayer properties in order to swiftly and easily convert misused vendor layers and colors to the required UNL standard layer and layer properties.  The standard UNL layer properties described herein are essential to internal reproduction of plans from department to department without the need for storing and managing vendor plot styles.

Similarly blocks, symbols and details shall also be created with bylayer properties and revert to layer 0 or bylayer properties when exploded.  Refer to the Blocks and Details section herein for additional information on the use and insertion of blocks within floor plans, drawings and/or xrefs.

## Text

### Text Descriptions

UNL FPC requires that all text associated with the drawing of building floor plans, elevations, enlarged floor plans, section, details, schedules, risers, notes, call-outs, dimensions and titles be represented a standard UNL text style and font as indicated in the table below.  All text height shown (unless noted otherwise) represents model space layout drawn at 1/8”=1’-0” scale.  Refer to the afore scale factor section herein for conversion of model space text height per respective scale factor.

### Text Style, Font and Size Table

| Use | Text Style | Font | Width | Model Space Height | Paper Space Height | Angle | Color | Orientation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Room, Space Name/No. | UNL-Dwg | Arial | 1.0 | 1’-0” | 1/8” | 18 | White 7 | 90° |
| Door No. | UNL-Dwg | Arial | 1.0 | 1’-0” | 1/8” | 0 | White 7 | 0° or 90° |
| Area SF | UNL-Dwg | Arial | 1.0 | 1’-6” | 3/16” | 18 | White 7 | 90° |
| Dimensions | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | White 7 | 0° or 90° |
| Leader Note | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | White 7 | 0° |
| General Note | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | White 7 | 0° |
| Keyed Note | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | White 7 | 0° |
| Equip. Tag Call Out | UNL-Dwg | Arial | .9 | 9” | 3/32” | 0 | White 7 | 0° or 90° |
| Demolition Text | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | White 7 | 0° |
| Existing to Remain Text | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | 145, 155 or 163 | 0° |
| Gen. Single Line Text | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | White 7 | 0° or 90° |
| Elevation/ Detail/ Section Text | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | White 7 | 0° |
| Riser Text | UNL-Dwg | Arial | 1.0 | 9” | 3/32” | 0 | White 7 | 0° or 90° |
| Note Titles | UNL-Dwg | Arial | 1.0 | 1’-0” | 1/8” | 0 | White 7 | 0° |
| Schedule Titles | UNL-Dwg | Arial | 1.0 | 1’-0” | 1/8” | 0 | Red 1 | 0° |
| Elevation/ Detail/ Section Titles | UNL-Dwg | Arial | 1.0 | 2’-0” | 1/4” | 0 | Red 1 | 0° |
| Plan & Sheet Titles | UNL-Dwg | Arial | 1.0 | 2’-0” | 1/4” | 0 | Red 1 | 0° |
| Title Block General Info | UNL-Dwg | Arial | 1.0 | --- | 1/8” | 0 | White 7 | 0° |
| Title Block Sheet Title & Projct.Name | UNL-Dwg | Arial | 1.0 | --- | 3/16” | 0 | White 7 | 0° |
| Title Block Sheet Numb | UNL-Dwg | Arial | 1.0 | --- | 3/8” | 0 | White 7 | 0° |
| All model space text sizes above are listed at 1/8”=1’-0” for reference, actual text sizes to be adjusted according to respective scale factors. Only the above text style, sizes and fonts are approved by UNL FPC, no frame, fill or non-standard AutoCAD® text shall be used. Alternate styles, sizes and fonts must have prior approval by UNL FPC. |  |  |  |  |  |  |  |  |

## Dimensioning

### Dimension Description

UNL FPC requires that all dimensioning be completed in model space.  Dimensioning shall also be completed in layer A-ANNO-DIMS, bylayer, white (7), continuous linetype and default lineweight.  UNL does not recognize the use of Interior (I) discipline designator layers for dimensions and request that this either not be used when at all possible or be converted to A-ANNO-DIMS layer upon output to AutoCAD.dwg delivery to UNL FPC.

### Dimension Style Parameters

UNL FPC suggests the use of the standard UNL FPC dimension style.  “UNL-DIM” dimension style is available for download and can be found in the CAD library downloads section with the new drawing title block templates.  UNL-DIM style parameters shall be set according to the following UNL FPC standard dimension styles:

Alternate Units parameters are not defined nor displayed for the UNL-DIM dimension style.

## Blocks, Details and Title Blocks

### Block Definitions

As active users of construction documents and As-Built drawings, UNL FPC plots, views, modifies and revises these plans regularly.  In order to efficiently and effectively use these drawings, all parameters of a CAD drawing including blocks, details, symbols and any other predefined entities shall have the ability to be easily modified.  UNL FPC modifies these drawings periodically for use with other department and program assessment needs as well as internal and external projects.  In doing this, it is required that the floor plan, background, blocks, details, symbols and other predefined entities be easily be manipulated to match the UNL FPC uniform standard layer and layer color assignments for best viewing and plotting.  Thus it’s imperative that all entities of a CAD drawing are easily able to be modified during later use.

It shall be required that all blocks, block definitions, details, hatch patterns, walls types, symbols, line types and other predefined entities including block attributes be created in layer 0 with bylayer properties.  All predefined block entities shall revert to layer 0 and Bylayer properties when exploded. Blocks created in layer 0 and bylayer properties shall be inserted into the CAD drawing and then placed in the respective layer for said entity.  All predefined entities created in programs other than AutoCAD® shall also revert to layer 0 and bylayer properties.  Avoid the use of nested blocks.

### UNL FPC Defined Blocks and Details

UNL FPC has created a library of general blocks and details specific to UNL projects.  Refer to the CAD library downloads section and utilize the blocks and details as required for respective project needs.

### Vendor Defined Blocks and Symbols

Utilize the US National CAD Standards V5, AIA, ASHRAE and SMACNA for user defined blocks and symbols.  Represent all Blocks and Symbols with a well-defined symbols legend sheet that accurately depicts these items.  Vendor defined blocks and symbols shall be created with bylayer properties and attributes and inserted into the drawing with the appropriate AIA CAD layering guideline.  When initially creating a user defined block or symbol, such entity shall be constructed such that it will revert back to layer 0 when exploded.  All predefined entities created in programs other than AutoCAD® shall also revert to layer 0 and Bylayer properties.

### UNL Title Blocks

UNL FPC requires the use of a standard UNL cover sheet and UNL title block.  The cover sheet and title blocks are available for download and can be found in the CAD library downloads section.  24”x36” and 30”x42” title block sheets are the standard size required by UNL FPC.  There may be times when it may become necessary to utilize a larger or alternate sized title block for special circumstances.  In the event an alternate sized title block is needed it shall be constructed similarly and with the same attributes as standard UNL title blocks.  The alternate title block shall be submitted and approved by UNL FPC prior to its use describing the reason to waiver away from the standard title blocks.

Supplemental design sheets, sketch sheets and revision sheets shall also be provided on a standard UNL FPC title block.  8.5”x11” and 11”x17” UNL supplemental title block sheets are available for download and can be found in the CAD library downloads section.

### UNL North Arrow

UNL FPC requires the use of a standard UNL north arrow, sheet title and detail/section/elevation title.  The north arrow and titles are available for download and can be found in the CAD library downloads section.  The north arrow is required to appear facing upward on all acceptable drawings.  There may be times when it may become necessary to utilize a true North arrow or Arrow appearing other than upward for special circumstances.  In the event an alternate directed North arrow is needed it shall be submitted and approved by UNL FPC project manager prior to its use describing the reason to waiver away from the standard up facing arrow.

### Addenda, Revisions

Construction revisions that impact a project’s drawing set including addendums, sketches, change directives and supplemental instructions/information shall be clearly documented and provided as part of the AutoCAD®.dwg construction drawing.  Any changes made to the original construction set of drawings shall be highlighted using a revision cloud and revision delta triangle.  These revisions indicators shall correspond with the revision section of the UNL FPC title block with matching numerical characters.

The addenda and/or revisions may be issued under separate cover and separate UNL FPC title block sheet.  8.5”x11” or 11”x17” sheets using the standard UNL FPC title block are recommended.  However, any size media to best suit the needs pertaining to those addenda will be acceptable.  The addenda are required to follow all standards as set forth herein as well as follow AIA documentation.  During construction or pre-construction these revisions shall become part of the final set of construction As-Built drawings.  Refer to Project Closeout section herein for additional information.

## Layers

### Layer Description

UNL FPC has adopted and requires the use of the most recent version of the AIA CAD Layer Guidelines found in the latest addition of the Unites States National CAD Standards.  Any and all additional vendor layers used shall strictly follow the AIA CAD Layer Guidelines procedure.  All drawing elements outside of the required UNL FPC layer and layer attributes shall be placed on respective AIA CAD standard layers.  User defined Bylayer properties are required for all elements and entities when assigning a layer to an element.  UNL does not recognize the use of Interior (I) discipline designator layers for any objects or elements and request that these either not be used when at all possible or be converted to a respective Architectural (A) discipline designator layer upon output to AutoCAD.dwg delivery to UNL FPC.

### AIA CAD Layer Naming Summary

1.0 Layer Name Format

1.1 HIERARCHY OF DATA FIELDS

The layer name format is organized as a hierarchy. This arrangement allows users to select from a number of options for naming layers according to the level of detailed information desired. Layer names consist of distinct data fields separated from one another by dashes. A detailed list of abbreviations, or field codes, is prescribed to define the content of layers. Most field codes are mnemonic English abbreviations of construction terminology that are

easy to remember.

There are four defined layer name data fields: Discipline Designator, Major Group, two Minor Groups, and Status. The Discipline Designator and Major Group fields are mandatory. The Minor Group and Status fields are optional. Each data field is separated from adjacent fields by a dash ("-") for clarity.

The complete NCS layer name format, showing the Discipline Designator, the Major Group, two Minor Groups, and the Status fields.

| A | I | - | W | A | L | L | - | F | U | L | L | - | D | I | M | S | - | N |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

1.2 BEFORE YOU BEGIN

The NCS allows you to select from a number of format options for creating layer names. It is recommended that you select the options that you wish to use for layer names on a given project, and then apply the resulting format consistently for all layer names on that project.

NOTE: For conceptual conformance to ISO 13567, Organization and Naming of Layers for CAD, the layer name format and length must be the same for all layers on a given project. See CLG Appendix C - Complying with NCS and ISO 13567, CLG section 6.0 for information about ISO conformance. Δ

1.3 DISCIPLINE DESIGNATOR, LEVEL 1

The Discipline Designator denotes the category of subject matter contained on the specified layer. The Discipline Designator is a two-character field. The first character is the discipline character, and the second character is an optional modifier. The Discipline

Designator is described in greater detail in UDS Section 1.3. For a complete list of Discipline Designators see CLG Appendix A - Discipline Designators, CLG section 4.1 and UDS Appendix A - Discipline Designators, UDS section 1.6.V 1 DISCIPLINE DESIGNATORS

A typical layer name showing the required data fields only.

| A | - | W | A | L | L |
| --- | --- | --- | --- | --- | --- |

Note that only the mandatory discipline character is shown, creating a Level 1 Discipline Designator.

A		Architectural

B		Geotechnical

C		Civil

D		Process

E		Electrical

F		Fire Protection

G		General

H		Hazardous Material

I		Interiors

L		Landscape

M		Mechanical

O		Operations

P		Plumbing

Q		Equipment

R		Resource

S		Structural

T		Telecommunication

V		Survey / Mapping

W		Distributed Energy

X		Other Disciplines

Z		Contractor / Shop Drawings

1.4 DISCIPLINE DESIGNATOR, LEVEL 2

The optional second character is used to further define the discipline character. As an example, the Level 2

Discipline Designators for Architectural are shown:

A	Architectural

AD	Architectural Demolition AE	Architectural Elements AF	Architectural Finishes AG	Architectural Graphics AI	Architectural Interiors AS	Architectural Site

AJ	User Defined

AK	User Defined

A typical layer name showing the required data fields only.

| A | D | - | W | A | L | L |
| --- | --- | --- | --- | --- | --- | --- |

Note that the mandatory Level 1 discipline character is supplemented by the optional discipline modifier to create a Level 2 Discipline Designator.

For a complete list of Discipline Designators see CLG Appendix A - List of Discipline Designators, Major and Minor

Groups, and Status Fields, CLG section 4.1 and UDS Appendix A - Discipline Designators, UDS section 1.6.

1.5 MAJOR GROUP

The major group is a four-character field that identifies a major building system. The prescribed Major Group field codes (four- character abbreviations) shown on the Layer List are logically grouped with specific discipline designators. However, any Major Group may be combined with any prescribed Discipline

Designator, provided that the definition of the Major Group remains

| A | - | W | A | L | L |
| --- | --- | --- | --- | --- | --- |

A typical layer name showing the required data fields only. The mandatory Major Group field is highlighted:

unchanged. Therefore, any reasonable combination of the prescribed Discipline Designators and Major

Groups is permitted.

NOTE: The NCS recognizes that there will be instances where user-defined Major Group field codes will be required. The NCS set of Major Group field codes is not intended to be all inclusive. There will be instances when project specific Major Groups will need to be created. In these cases Major Group field codes are allowed, however, they must contain four alphabetic and/or numeric characters and/or "~", and must be fully documented on the NCS Compliance Disclosure Statement for the project or identified as project specific in the standard supplement in

which they are used.

NOTE: For conceptual conformance to ISO 13567, Organization and Naming of Layers for CAD, the use of the

Major Group "ANNO" is not permitted. See CLG Appendix C - Complying with NCS and ISO 13567, CLG section

6.0 for information about ISO conformance. Δ

1.6 MINOR GROUP

This is an optional, four-character field to further define the Major Groups. For example, A-WALL-FULL denotes Architectural, Wall, Full-height. A second minor group may be used for still further delineation of the data contained on a layer. For example,

A-WALL-FULL TEXT indicates Architectural, Wall, Full-height, Text.

The prescribed Minor Group field codes (four-character abbreviations) shown on the Layer List are logically grouped with specific Major Groups. However, any Minor Group may be used to modify any Major Group, provided that the definition of the Minor Group remains unchanged. Therefore, any reasonable

combination of the prescribed Major and Minor Groups is permitted.

A typical layer name showing one optional Minor Group field:

| A | - | W | A | L | L | - | F | U | L | L |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

A typical layer name showing two optional Minor Group fields:

| A | - | W | A | L | L | - | F | U | L | L | - | T | E | X | T |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

NOTE: User-defined Minor Group field codes are permitted. They must contain four alphabetic and/or numeric characters and/or "~", and must be fully documented on the NCS Compliance Disclosure Statement for the project

on which they are used.

NOTE: For conceptual conformance to ISO 13567, Organization and Naming of Layers for CAD, the use of certain

Minor Group field codes is restricted. See CLG Appendix C - Complying with NCS and ISO 13567, CLG section 6.0

for information about ISO conformance. Δ

1.7 STATUS (PHASE)

The status field is an optional single-character field that distinguishes the data contained on the layer according to the status of the work or the construction phase. The prescribed field codes for this field are as follows:

STATUS D CODES

A typical layer name showing the location of the optional

| A | - | W | A | L | L | - | F | U | L | L | - | T | E | X | T | - | N |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Status field:

A 	Abandoned

D 	Existing to demolish

E 	Existing to remain

F 	Future work

M 	Items to be moved

N 	New Work

T 	Temporary work

X	Not in contract

1-9	Phase numbers

National Institute of Building Sciences | An Authoritative Source of Innovative Solutions for the Built Environment

1090 Vermont Avenue, NW, Suite 700 | Washington, DC 20005-4950 | (202) 289-7800 | Fax (202) 289-1092

© 2011 National Institute of Building Sciences. All rights reserved.

### UNL FPC Layer Properties

In addition to the use of AIA CAD Layer Guidelines, UNL FPC has supplemented specific CAD layer properties and attributes which are extensively used internally for program assessment, space management and future project development.  In addition to vendors following the AIA national CAD standard layer guidelines; the below are the predefined UNL layer properties used internally by FPC.  It is imperative that the bold and dark highlighted (A) Architectural layers and layer attributes be implemented and strictly followed on all projects upon output of AutoCAD®.dwg files delivered to UNL FPC either for progress submittal, final construction submittal or “as-built” documentation. Take note that UNL FPC does not implement the use of the (I) Interiors layer discipline designation.  These specific UNL FPC layers properties listed below and strictly required to be followed are necessary for internal use within the University and further described herein this document.

### UNL FPC Layer Property Table

| Name | Description | Color | Linetype | Plotted Lineweight |
| --- | --- | --- | --- | --- |
| 0 |  | 7 | Continuous | 0.15mm |
| A-ANNO-AREA-IDEN | Architectural area square foot identification | 6 | Continuous | 0.15mm |
| A-ANNO-DETL-TEXT | General architectural detail text | 7 | Continuous | 0.15mm |
| A-ANNO-DIMS | Architectural Dimensions | 7 | Continuous | 0.15mm |
| A-ANNO-DOOR-IDEN | Door identification | 7 | Continuous | 0.15mm |
| A-ANNO-GLAZ-IDEN | Glazing, window identification | 7 | Continuous | 0.15mm |
| A-ANNO-KEYN | Architectural keynote | 7 | Continuous | 0.15mm |
| A-ANNO-LEGN | Architectural legend | 7 | Continuous | 0.15mm |
| A-ANNO-LOGO | Architectural consultant logo | 7 | Continuous | 0.15mm |
| A-ANNO-NOTE | Architectural sheet notes | 7 | Continuous | 0.15mm |
| A-ANNO-NPLT | Non-plotting graphic information | 5 | Continuous | 0.20mm |
| A-ANNO-REVC | Architectural revision clouds | 11 | Continuous | 0.70mm |
| A-ANNO-REVS | Architectural revision indicators and text | 241 | Continuous | 0.50mm |
| A-ANNO-ROOM-IDEN | Architectural room identification | 7 | Continuous | 0.15mm |
| A-ANNO-SCHD | Architectural schedules | 7 | Continuous | 0.15mm |
| A-ANNO-STMP | Architectural professional stamps | 7 | Continuous | 0.15mm |
| A-ANNO-SYMB | Architectural reference symbols | 7 | Continuous | 0.15mm |
| A-ANNO-TEXT | General architectural text | 7 | Continuous | 0.15mm |
| A-AREA | Area polyline | 6 | Continuous | 0.15mm |
| A-CLNG | Ceiling | 9 | Continuous | 0.10mm |
| A-CLNG-ACCS | Ceiling: access | 212 | Continuous | 0.10mm |
| A-CLNG-GRID | Ceiling: grid | 9 | Continuous | 0.10mm |
| A-CLNG-SUSP | Ceiling: suspended elements | 212 | Continuous | 0.10mm |
| A-COLS | Columns | 7 | Continuous | 0.15mm |
| A-DETL | Details | 6 | Continuous | 0.15mm |
| A-DETL-BYND | Detail hatch patterns, objects beyond | 8 | Continuous | 0.05mm 50% Screen |
| A-DOOR | Doors | 1 | Continuous | 0.35mm |
| A-EQPM | Equipment | 30 | Continuous | 0.15mm |
| A-EQPM-OVHD | Equipment: overhead | 30 | Dashed | 0.15mm |
| A-FLOR | Floor | 9 | Continuous | 0.10mm |
| A-FLOR-CSWK | Floor: casework | 8 | Continuous | 0.05mm 50% Screen |
| A-FLOR-EVTR | Floor: elevator cars and equipment | 151 | Continuous | 0.05mm |
| A-FLOR-FIXT | Floor: fixtures (plumbing) | 151 | Continuous | 0.05mm |
| A-FLOR-OTLN | Floor: outline | 9 | Continuous | 0.10mm |
| A-FLOR-OVHD | Floor: overhead | 9 | Dashed | 0.10mm |
| A-FLOR-SIGN | Floor: signage | 2 | Continuous | 0.25mm |
| A-FLOR-STRS | Floor: stair treads (escalators, ladders) | 151 | Continuous | 0.05mm |
| A-FLOR-TPTN | Floor: toilet partitions | 151 | Continuous | 0.05mm |
| A-FURN | Furnishings | 8 | Continuous | 0.05 50% Screen |
| A-FURN-STOR | Furnishings: storage (component system) | 8 | Continuous | 0.05 50% Screen |
| A-GLAZ | Glazing, windows | 2 | Continuous | 0.25mm |
| A-HTCH-PATT | Textures & hatch patterns excluding walls | 9 | Continuous | 0.10mm |
| A-HVAC | HVAC systems | 3 | Continuous | 0.25mm |
| A-HVAC-CDFF | HVAC system: Diffuser, Grille, & Register | 3 | Continuous | 0.25mm |
| A-LITE | Lighting | 3 | Continuous | 0.25mm |
| A-ROOF | Roof | 9 | Continuous | 0.10mm |
| A-ROOF-HRAL | Roof: handrails/guard rails | 1 | Continuous | 0.35mm |
| A-ROOF-OTLN | Roof: outline | 9 | Continuous | 0.10mm |
| A-ROOF-STRS | Roof: stair treads (ladders) | 151 | Continuous | 0.05mm |
| A-WALL | Walls | 1 | Continuous | 0.35mm |
| A-WALL-CURT | Walls: curtain | 151 | Continuous | 0.05mm |
| A-WALL-FIRE | Walls: fire protection | 101 | Continuous | 0.25mm |
| A-WALL-HEAD | Walls: Header, doors, windows | 8 | Continuous | 0.05mm 50% Screen |
| A-WALL-PATT | Walls: texture and hatch patterns | 9 | Continuous | 0.10mm |
| Defpoints | Non-plotting information | 8 | Continuous | ---- |
| E-ALRM | Alarm system | 121 | Continuous | 0.25mm |
| E-ANNO-DETL-TEXT | General electrical detail/riser text | 7 | Continuous | 0.15mm |
| E-ANNO-DIMS | Electrical Dimensions | 7 | Continuous | 0.15mm |
| E-ANNO-IDEN | General electrical identification | 7 | Continuous | 0.15mm |
| E-ANNO-KEYN | Electrical keynote | 7 | Continuous | 0.15mm |
| E-ANNO-LEGN | Electrical legend | 7 | Continuous | 0.15mm |
| E-ANNO-LITE-IDEN | Lighting device/equip. identification | 7 | Continuous | 0.15mm |
| E-ANNO-LOGO | Electrical consultant logo | 7 | Continuous | 0.15mm |
| E-ANNO-NOTE | Electrical sheet notes | 7 | Continuous | 0.15mm |
| E-ANNO-NPLT | Non-plotting graphic information | 5 | Continuous | 0.20mm |
| E-ANNO-POWR-IDEN | Power device/equip. identification | 7 | Continuous | 0.15mm |
| E-ANNO-REVC | Electrical revision clouds | 11 | Continuous | 0.70mm |
| E-ANNO-REVS | Electrical revision indicators and text | 241 | Continuous | 0.50mm |
| E-ANNO-SCHD | Electrical schedules | 7 | Continuous | 0.15mm |
| E-ANNO-STMP | Electrical professional stamps | 7 | Continuous | 0.15mm |
| E-ANNO-TEXT | General electrical text | 7 | Continuous | 0.15mm |
| E-AUXL | Auxiliary systems | 150 | Continuous | 0.25mm |
| E-BELL | Bell system | 150 | Continuous | 0.25mm |
| E-CABL-TRAY | Cable systems: cable tray and wire ways | 30 | Dashed | 0.15mm |
| E-CATV | Cable TV system | 114 | Continuous | 0.25mm |
| E-CCTV | Closed-circuit television system | 121 | Continuous | 0.25mm |
| E-CLOK | Clock system | 150 | Continuous | 0.25mm |
| E-COMM | Communications | 114 | Continuous | 0.25mm |
| E-COMM-EQPM | Communications: equipment | 114 | Continuous | 0.25mm |
| E-CONT | Controls and instrumentation | 150 | Continuous | 0.25mm |
| E-CONT-WIRE | Controls and instrumentation: wiring | 150 | Continuous | 0.25mm |
| E-DATA | Data/LAN system | 114 | Continuous | 0.25mm |
| E-DATA-EQPM | Data/LAN system: equipment | 114 | Continuous | 0.25mm |
| E-DETL | Details | 6 | Continuous | 0.15mm |
| E-DETL-BYND | Detail hatch patterns, objects beyond | 8 | Continuous | 0.05mm 50% Screen |
| E-FIRE | Fire protection | 101 | Continuous | 0.25mm |
| E-GRND | Ground system | 30 | Continuous | 0.15mm |
| E-INTC | Intercom system | 150 | Continuous | 0.25mm |
| E-LITE | Lighting | 4 | Continuous | 0.25mm |
| E-LITE-CIRC | Lighting: circuits | 2 | Continuous | 0.25mm |
| E-LITE-CIRC-EMER | Lighting: circuits: emergency | 125 | Continuous | 0.25mm |
| E-LITE-CNMB | Lighting: circuit number | 7 | Continuous | 0.15mm |
| E-LITE-CNMB-EMER | Lighting: circuit number: emergency | 7 | Continuous | 0.15mm |
| E-LITE-EMER | Lighting: emergency | 125 | Continuous | 0.25mm |
| E-LITE-EXIT | Lighting: exit | 125 | Continuous | 0.25mm |
| E-LITE-SWCH | Lighting: switches | 4 | Continuous | 0.25mm |
| E-LTNG | Lightning protection system | 3 | Continuous | 0.25mm |
| E-MNTG | Electrical mounting system | 30 | Continuous | 0.25mm |
| E-POWR | Power | 3 | Continuous | 0.25mm |
| E-POWR-CIRC | Power: circuits | 41 | Continuous | 0.25mm |
| E-POWR-CIRC-EMER | Power: circuits: emergency | 41 | Continuous | 0.25mm |
| E-POWR-CNMB | Power: circuit number | 7 | Continuous | 0.15mm |
| E-POWR-CNMB-EMER | Power: circuit number: emergency | 7 | Continuous | 0.15mm |
| E-POWR-EQPM | Power: equipment | 30 | Continuous | 0.15mm |
| E-POWR-EQPM-EMER | Power: equipment: emergency | 30 | Continuous | 0.15mm |
| E-POWR-PANL | Power: panels | 30 | Continuous | 0.15mm |
| E-POWR-SWBD | Power: switchboards | 30 | Continuous | 0.15mm |
| E-POWR-XFMR | Power: transformers: pad-mounted | 30 | Continuous | 0.15mm |
| E-SECU | Security system | 121 | Continuous | 0.25mm |
| E-SITE | Site features | 4 | Continuous | 0.25mm |
| E-SITE-OVHD | Site: overhead | 2 | Continuous | 0.25mm |
| E-SITE-POLE | Site: pole | 30 | Continuous | 0.15mm |
| E-SITE-UGND | Site: underground | 41 | Hidden | 0.25mm |
| E-SOUN | Sound system | 150 | Continuous | 0.25mm |
| E-UTIL | Utilities | 30 | Hidden | 0.15mm |
| F-SPKL-EQPM | Fire Suppression Equipment | 30 | Continuous | 0.15mm |
| F-SPKL-EQPM-POWR | Fire Suppression Equipment With Power | 30 | Continuous | 0.15mm |
| F-SPKL-HEAD | Fire Suppression Heads | 32 | Continuous | 0.25mm |
| F-SPKL-PIPE | Fire Suppression Piping | 32 | Continuous | 0.25mm |
| G-ANNO-KEYN | Keynotes | 7 | Continuous | 0.15mm |
| G-ANNO-LOGO | Consultant logo | 7 | Continuous | 0.15mm |
| G-ANNO-MATC | Match lines | 11 | Phantom | 0.70mm |
| G-ANNO-NOTE | Notes | 7 | Continuous | 0.15mm |
| G-ANNO-PLAN | Key plan | 7 | Continuous | 0.15mm |
| G-ANNO-REFR | Reference, external files | 7 | Continuous | 0.15mm |
| G-ANNO-SYMB | Reference symbols | 7 | Continuous | 0.15mm |
| G-ANNO-TITL | Drawing or detail titles - scarlet red | 240 | Continuous | 0.25mm |
| G-ANNO-TTLB | Border and title block | 7 | Continuous | 0.15mm |
| G-ANNO-TTLB-IDEN | Title block identification | 7 | Continuous | 0.15mm |
| G-ANNO-TTLB-INFO | Title block information - scarlet red | 7 | Continuous | 0.25mm |
| G-ANNO-TTLB-TEXT | Title block text - scarlet red | 240 | Continuous | 0.25mm |
| M-ANNO-DETL-TEXT | Details, Risers, and Schematics Text | 7 | Continuous | 0.15mm |
| M-ANNO-DIMS | Mechanical dimensions | 7 | Continuous | 0.15mm |
| M-ANNO-EQPM-IDEN | Equipment Marks/Identification Text | 7 | Continuous | 0.15mm |
| M-ANNO-IDEN | General Mechanical Identification Text | 7 | Continuous | 0.15mm |
| M-ANNO-KEYN | Mechanical Keynote | 7 | Continuous | 0.15mm |
| M-ANNO-LEGN | Legends and Symbol Keys | 7 | Continuous | 0.15mm |
| M-ANNO-LOGO | Mechanical consultant logo | 7 | Continuous | 0.15mm |
| M-ANNO-NOTE | Mechanical sheet notes | 7 | Continuous | 0.15mm |
| M-ANNO-NPLT | Non-Plotting Graphic Information | 5 | Continuous | 0.20mm |
| M-ANNO-REVC | Mechanical revision Clouds | 11 | Continuous | 0.70mm |
| M-ANNO-REVS | Mechanical revision Indicators and Text | 241 | Continuous | 0.50mm |
| M-ANNO-SCHD | Mechanical schedules | 7 | Continuous | 0.15mm |
| M-ANNO-STMP | Mechanical professional Stamp | 7 | Continuous | 0.15mm |
| M-ANNO-TEXT | General Mechanical Text | 7 | Continuous | 0.15mm |
| M-CONT | Controls and Instrumentation | 191 | Continuous | 0.25mm |
| M-CWTR | Chilled Water Piping | 32 | Continuous | 0.25mm |
| M-DETL | Mechanical Details, Risers, & Schematics | 6 | Continuous | 0.15mm |
| M-DETL-BYND | Detail hatch patterns, objects beyond | 8 | Continuous | 0.05mm 50% Screen |
| M-HTPM | Heat Pump Piping | 205 | Continuous | 0.25mm |
| M-HVAC-CDFF | Ceiling Diffusers, Grilles, and Registers | 190 | Continuous | 0.25mm |
| M-HVAC-DMPR | Fire/Smoke Dampers | 211 | Continuous | 0.25mm |
| M-HVAC-EQPM | HVAC Equipment | 30 | Continuous | 0.15mm |
| M-HVAC-EQPM-POWR | HVAC Equipment With Power | 30 | Continuous | 0.15mm |
| M-HVAC-EXHS | Exhaust Ductwork | 54 | Continuous | 0.25mm |
| M-HVAC-OAIR | Outside Air Ductwork | 245 | Continuous | 0.25mm |
| M-HVAC-RAIR | Relief Air Ductwork | 54 | Continuous | 0.25mm |
| M-HVAC-RETN | Return Ductwork | 42 | Continuous | 0.25mm |
| M-HVAC-SPLY | Supply Ductwork | 34 | Continuous | 0.25mm |
| M-HWTR | Hot Water Piping | 214 | Continuous | 0.25mm |
| M-REFG | Refrigerant Piping | 224 | Continuous | 0.25mm |
| M-STEM | Steam Piping | 210 | Continuous | 0.25mm |
| M-STEM-CONS | Steam Condensate Piping | 244 | Continuous | 0.25mm |
| P-ANNO-DETL-TEXT | Details, Risers, and Schematics Text | 7 | Continuous | 0.15mm |
| P-ANNO-DIMS | Plumbing Dimensions | 7 | Continuous | 0.15mm |
| P-ANNO-EQPM-IDEN | Equipment Marks/Identification Text | 7 | Continuous | 0.15mm |
| P-ANNO-IDEN | General Plumbing Identification Text | 7 | Continuous | 0.15mm |
| P-ANNO-KEYN | Plumbing Keynote | 7 | Continuous | 0.15mm |
| P-ANNO-LEGN | Legends and Symbol Keys | 7 | Continuous | 0.15mm |
| P-ANNO-LOGO | Mechanical consultant logo | 7 | Continuous | 0.15mm |
| P-ANNO-NOTE | Plumbing sheet notes | 7 | Continuous | 0.15mm |
| P-ANNO-NPLT | Non-Plotting Graphic Information | 5 | Continuous | 0.20mm |
| P-ANNO-REVC | Plumbing revision Clouds | 11 | Continuous | 0.70mm |
| P-ANNO-REVS | Plumbing revision Indicators and Text | 241 | Continuous | 0.50mm |
| P-ANNO-SCHD | Plumbing schedules | 7 | Continuous | 0.15mm |
| P-ANNO-STMP | Mechanical professional Stamp | 7 | Continuous | 0.15mm |
| P-ANNO-TEXT | General Plumbing Text | 7 | Continuous | 0.15mm |
| P-DETL | Plumbing Details, Risers, and Schematics | 6 | Continuous | 0.15mm |
| P-DETL-BYND | Detail hatch patterns, objects beyond | 8 | Continuous | 0.05mm 50% Screen |
| P-DOMW-CPIP | Domestic Cold Water Piping | 150 | Cold_Water | 0.25mm |
| P-DOMW-HPIP | Domestic Hot Water Piping | 150 | Hot_Water | 0.25mm |
| P-DOMW-RPIP | Domestic Hot Water Recirc. Piping | 150 | Recirc | 0.25mm |
| P-EQPM | Plumbing Equipment | 30 | Continuous | 0.15mm |
| P-EQPM-POWR | Plumbing Equipment With Power | 30 | Continuous | 0.15mm |
| P-GAS~ | Gas Piping | 242 | Continuous | 0.25mm |
| P-INDL | Industrial Water Piping (Non Potable) | 233 | Continuous | 0.25mm |
| P-SSWR | Sanitary Sewer Piping | 82 | Continuous | 0.25mm |
| P-STRM | Storm Sewer Piping | 10 | Continuous | 0.25mm |
| P-VENT | Vent Piping | 204 | Continuous | 0.25mm |
| S-ANNO-DETL-TEXT | Details, Risers, and Schematics Text | 7 | Continuous | 0.15mm |
| S-ANNO-DIMS | Structural dimensions | 7 | Continuous | 0.15mm |
| S-ANNO-IDEN | Structural identification text | 7 | Continuous | 0.15mm |
| S-ANNO-KEYN | Structural keynote | 7 | Continuous | 0.15mm |
| S-ANNO-LEGN | Structural legends and symbol keys | 7 | Continuous | 0.15mm |
| S-ANNO-LOGO | Structural consultant logo | 7 | Continuous | 0.15mm |
| S-ANNO-NOTE | Structural sheet notes | 7 | Continuous | 0.15mm |
| S-ANNO-NPLT | Non-Plotting Graphic Information | 5 | Continuous | 0.20mm |
| S-ANNO-REVC | Structural revision clouds | 11 | Continuous | 0.70mm |
| S-ANNO-REVS | Structural revision indicators and text | 241 | Continuous | 0.50mm |
| S-ANNO-SCHD | Structural schedules | 7 | Continuous | 0.15mm |
| S-ANNO-STMP | Structural professional stamp | 7 | Continuous | 0.15mm |
| S-ANNO-SYMB | Structural reference symbols | 7 | Continuous | 0.15mm |
| S-ANNO-TEXT | General structural text | 7 | Continuous | 0.15mm |
| S-BEAM | Structural: Beams | 135 | Dashed | 0.25mm |
| S-BRCG | Structural: Bracing | 167 | Continuous | 0.25mm |
| S-COLS | Structural: Columns | 135 | Continuous | 0.25mm |
| S-DECK | Structural: Deck | 167 | Continuous | 0.25mm |
| S-DETL | Structural: Detail | 6 | Continuous | 0.15mm |
| S-DETL-BYND | Detail hatch patterns, objects beyond | 8 | Continuous | 0.05mm 50% Screen |
| S-FNDN | Structural: Foundation | 15 | Continuous | 0.25mm |
| S-FNDN-FTNG | Structural: Foundation footings | 15 | Hidden | 0.25mm |
| S-GRID | Structural: Grids | 8 | Center2 | 0.05mm 50% Screen |
| S-GRLN | Structural: Grade line | 3 | Continuous | 0.25mm |
| S-JNTS | Structural: Joints | 15 | Continuous | 0.25mm |
| S-JOIS | Structural: Joists | 135 | Center2 | 0.25mm |
| S-LNTL | Structural: Lintels | 9 | Dashed | 0.10mm |
| S-PADS-EQPM | Structural Pads: equipment | 9 | Continuous | 0.10mm |
| S-PLAT | Structural: Platform | 9 | Dashed | 0.10mm |
| S-PLAT-GRTG | Structural: Platform grating | 9 | Continuous | 0.10mm |
| S-SLAB-CONC | Structural: Slab, concrete | 15 | Continuous | 0.25mm |
| S-STRS | Structural: Stairs | 151 | Continuous | 0.05mm |
| S-TRUS | Structural: Trusses | 135 | Hidden | 0.25mm |
| S-WALL | Structural: Walls | 1 | Continuous | 0.35mm |
| (A) w/Status Indicator | Demo, New and Existing Layers |  |  |  |
| A-DOOR-D | Existing to demolish doors | 1 | Continuous | 0.35mm |
| A-DOOR-N | New doors, used when existing layers do not utilize the ‘E’ (existing) status indicator | 1 | Continuous | 0.35mm |
| A-GLAZ-D | Existing to demolish glazing, windows | 2 | Continuous | 0.25mm |
| A-GLAZ-N | New glazing, used when existing layers do not utilize the ‘E’ (existing) status indicator | 2 | Continuous | 0.25mm |
| A-WALL-D | Existing to demolish walls | 1 | Continuous | 0.35mm |
| A-WALL-N | New walls, used when existing layers do not utilize the ‘E’ (existing) status indicator | 1 | Continuous | 0.35mm |
| A-~~~~-~~~~-D | Existing to demolish specific Architectural ceilings, walls, structure, outlines | Copy Main Layr | Copy Main Layr | 0.25mm |
| A-~~~~-~~~~-D | Existing to demolish specific Architectural devices, furnishings, doors, glazing | Copy Main Layr | Copy Main Layr | 0.25mm |
| A-~~~~-~~~~-E | Existing to remain specific Architectural ceilings, walls, structure, outlines, text | 145 | Existing | 0.05mm |
| A-~~~~-~~~~-E | Existing to remain specific Architectural devices, furnishings, doors, glazing | 31 | Existing | 0.05mm |
| A-~~~~-~~~~-N | New Architectural, used when existing layers do not utilize the ‘E’ (existing) status indicator | Copy Main Layr | Copy Main Layr | 0.25mm |
| (E) w/Status Indicator | Demo, New and Existing Layers |  |  |  |
| E-LITE-D | Existing to demolish lighting items | 4 | Continuous | 0.25mm |
| E-LITE-E | Existing to remain lighting items | 155 | Existing | 0.05mm |
| E-POWR-D | Existing to demolish power items | 3 | Continuous | 0.25mm |
| E-POWR-E | Existing to remain power items | 33 | Existing | 0.05mm |
| E-AUXL-D | Existing to demolish low voltage items | 150 | Continuous | 0.25mm |
| E-AUXL-E | Existing to remain low voltage items | 33 | Existing | 0.05mm |
| E-~~~~-~~~~-D | Existing to demolish specific Electrical Routings, text | Copy Main Layr | Copy Main Layr | 0.25mm |
| E-~~~~-~~~~-D | Existing to demolish specific Electrical Equipment | Copy Main Layr | Copy Main Layr | 0.25mm |
| E-~~~~-~~~~-E | Existing to remain specific Electrical Routings, text | 155 | Existing | 0.05mm |
| E-~~~~-~~~~-E | Existing to remain specific Electrical Equipment | 33 | Existing | 0.05mm |
| E-~~~~-~~~~-N | New Electrical, used when existing layers do not utilize the ‘E’ (existing) status indicator | Copy Main Layr | Copy Main Layr | 0.25mm |
| (M) w/Status Indicator | Demo, New and Existing Layers |  |  |  |
| M-HVAC-D | Existing to demolish HVAC items | 190 | Continuous | 0.25mm |
| M-HVAC-E | Existing to remain HVAC items | 43 | Existing | 0.05mm |
| M-~~~~-~~~~-D | Existing to demolish specific Mechanical Routing, text | Copy Main Layr | Copy Main Layr | 0.25mm |
| M-~~~~-~~~~-D | Existing to demolish specific Mechanical Equipment | Copy Main Layr | Copy Main Layr | 0.25mm |
| M-~~~~-~~~~-E | Existing to remain specific Mechanical Routings, text | 163 | Existing | 0.05mm |
| M-~~~~-~~~~-E | Existing to remain specific Mechanical Equipment | 43 | Existing | 0.05mm |
| M-~~~~-~~~~-N | New Mechanical, used when existing layers do not utilize the ‘E’ (existing) status indicator | Copy Main Layr | Copy Main Layr | 0.25mm |
| (P) w/Status Indicator | Demo, New and Existing Layers |  |  |  |
| P-PLUM-D | Existing to demolish plumbing items | 150 | Continuous | 0.25mm |
| P-PLUM-E | Existing to remain plumbing items | 163 | Existing | 0.05mm |
| P-~~~~-~~~~-D | Existing to demolish specific Plumbing Routings, text | Copy Main Layr | Copy Main Layr | 0.25mm |
| P-~~~~-~~~~-D | Existing to demolish specific Plumbing Equipment | Copy Main Layr | Copy Main Layr | 0.25mm |
| P-~~~~-~~~~-E | Existing to remain specific Plumbing Routings, text | 163 | Existing | 0.05mm |
| P-~~~~-~~~~-E | Existing to remain specific Plumbing Equipment | 43 | Existing | 0.05mm |
| P-~~~~-~~~~-N | New Plumbing, used when existing layers do not utilize the ‘E’ (existing) status indicator | Copy Main Layr | Copy Main Layr | 0.25mm |

### Layer Attributes

The predefined layers and attributes listed in the UNL Layer Property Table herein have been assigned specific colors and line types.  These bold highlighted attributes are critical pieces, extensively used internally with “as-built” construction drawings.  The “as-built” construction drawings become part of the building plan “library of record” at UNL FPC.  Implementing and following these layers and layer attributes are strictly required when delivering electronic copies of AutoCAD®.dwg files to UNL FPC.  In order for UNL FPC to seamlessly pass along accurate building data to all departments within the University on a daily basis and print or otherwise manipulate the drawings; the said layer property table must be implemented upon delivery of AutoCAD®.dwg files to UNL FPC.   Layers and layer attributes that have not been predefined may be assigned at the discretion of the user following the exact AIA CAD Layering Guidelines found in the most current addition of the National CAD Standards Guidelines.

### Layer Colors

The bold highlighted layers and layer colors found in the predefined UNL Layer Property Table are specific to the layers and colors most often used to assist in University space documentation.  All other layers and layer colors may be assigned at the discretion of the vendor to meet their individual needs.  Coordinate and consider the selection of non-UNL required layer colors with the University plotted pen color lineweights found herein this document.

As a general rule for all CAD projects, drawings should assume the color property of the layer on which they reside.  The color of individual entities should be assigned “bylayer” as opposed to “by entity.”  Likewise, it shall be required that all blocks, block definitions, details, hatch patterns, walls types, symbols, line types and other predefined entities including block attributes be created with Bylayer properties.  All user defined entities shall revert to layer 0 and Bylayer properties when exploded. Blocks created in layer 0 and Bylayer properties shall be inserted into the CAD drawing and then placed in the respective layer for said entity.  All predefined entities created in programs other than AutoCAD® shall also revert to layer 0 and Bylayer properties.

### Layer Linetypes

The UNL FPC default linetype for each predefined layer is typically CONTINUOUS unless otherwise specified.  Linetype file UNL.lin (includes linetypes defined as Existing, Cold_Water, Hot_Water, and Recirc.) is available for download in the CAD library downloads sections.  All other layers may have their linetypes assigned at the discretion of the user.

### Layer Lineweight

The UNL FPC default lineweight for each predefined layer is typically DEFAULT 0.00.  Furthermore, UNL FPC utilizes plotted pen lineweights associated with respective colors to produce the desired lineweight thickness.  All vendor defined layers may have their lineweights assigned at the discretion of the user either via lineweight properties or utilizing the UNL color assignments.  Coordinate and consider the selection of non-UNL required layer lineweights with the University plotted pen color line weights found herein.

# CAD Templates

## Text, Notes, Fonts Hyperlink

## Dimension Style Hyperlink

## Blocks, Details Hyperlink

## Title Blocks, Sheet Sizes, Sheet Titles Hyperlink

## Standard UNL Layers Hyperlink

## Drawing Templates Hyperlink

## Plot Styles Hyperlink

# UNL Space & Planning Requirements

## Room Numbering

Refer to the room numbering convention in the University design guidelines and provide as necessary per all requirements.  Room/Space/Area names shall be provided on appropriate layers and in the text style, font and size as listed in the text table herein this document.

## Door Numbers

Refer to the door numbering convention in the University design guidelines and provide as necessary per all requirements.  Door numbers shall be provided on appropriate layers and in the text style, font and size as listed in the text table herein this document.

## Room and Space Area

Each room, space, area, corridor, vestibule and any other occupy able space shall be individually enclosed by a continuously joined polyline.

Archibus Program (see C:\Users\lsteigerjr2\Desktop\CAD Standards\Examples\Spec Items\University of Ill - Chicago\UofICADStandardsManual-2010-07.pdf

# CAD Reproduction

## UNL Drawing File Disclaimer

All construction documents must include the following UNL disclaimer: “These drawings and the designs here illustrated are the sole property of the University of Nebraska and may not be reproduced in whole or in part without express written permission.”

## Plot Styles

UNL FPC does not maintain, manage or store vendor AutoCAD® plot styles.  The plot style used by UNL is color-dependent (.CTB) files that set the style based on the color of the objects.  As described in the previous Layer section herein it is required that all vendors follow the bold, highlighted layers found in the UNL Layer Property Tables for AutoCAD®.dwg delivery to UNL FPC.  By using the UNL predefined layers and layer colors the internal University departments are assured of reproducing archived drawings that best depict the original intent of the drawing plans.  The UNL.CTB file is available for download and can be found in the CAD library downloads section in the event a vendor chooses to supplement the UNL .CTB file in lieu of their own plot style settings.

## UNL FPC Color and Line Weights

| Color | Plotted Lineweight | Color | Plotted Lineweight |
| --- | --- | --- | --- |
| RED 1 | 0.35mm | ACAD 135 | 0.25mm |
| YELLOW 2 | 0.25mm | ACAD 140 | 0.40mm |
| GREEN 3 | 0.25mm | ACAD 142 | 0.80mm |
| CYAN 4 | 0.25mm | ACAD 145 | 0.05mm |
| BLUE 5 | 0.20mm | ACAD 150 | 0.25mm |
| MAGENTA 6 | 0.15mm | ACAD 151 | 0.05mm |
| WHITE 7 | 0.15mm | ACAD 155 | 0.05mm |
| DARK GRAY 8 | 0.05mm 50% Screen | ACAD 163 | 0.05mm |
| LIGHT GRAY 9 | 0.10mm | ACAD 167 | 0.25mm |
| ACAD 10 | 0.25mm | ACAD 190 | 0.25mm |
| ACAD 11 | 0.70mm | ACAD 191 | 0.25mm |
| ACAD 15 | 0.25mm | ACAD 200 | 0.40mm |
| ACAD 30 | 0.15mm | ACAD 204 | 0.25mm |
| ACAD 31 | 0.05mm | ACAD 205 | 0.25mm |
| ACAD 32 | 0.25mm | ACAD 210 | 0.25mm |
| ACAD 33 | 0.05mm | ACAD 211 | 0.25mm |
| ACAD 34 | 0.25mm | ACAD 212 | 0.10mm |
| ACAD 41 | 0.25mm | ACAD 214 | 0.25mm |
| ACAD 42 | 0.25mm | ACAD 220 | 0.60mm |
| ACAD 43 | 0.05mm | ACAD 224 | 0.25mm |
| ACAD 54 | 0.25mm | ACAD 233 | 0.25mm |
| ACAD 62 | 0.60mm | ACAD 240 | 0.25mm |
| ACAD 81 | 0.80mm | ACAD 241 | 0.50mm |
| ACAD 82 | 0.25mm | ACAD 242 | 0.25mm |
| ACAD 101 | 0.25mm | ACAD 244 | 0.25mm |
| ACAD 114 | 0.25mm | ACAD 245 | 0.25mm |
| ACAD 121 | 0.25mm | All Other Colors | 0.20mm |
| ACAD 125 | 0.25mm |  |  |

## Printing

Prepared progress submittals, final construction documents or “as-built” documents shall be printed from paper space layout.  Each paper space layout page shall have settings saved in the Page Setup Manager.  Printer/plotter, paper size, paper area, plot scale, drawing orientation, layout viewports and a completed title block are the parameters that shall be set within the page setup manager.

A vendor’s final plot shall be accomplished using the vendor defined color-dependent plot style (.CTB) or named plot styles (.SB) to determine the characteristics of their object lineweights.  However, final output of AutoCAD®.dwg electronic files delivered to UNL FPC shall be capable of being printed with the UNL.CTB file, thus the layering must follow the UNL FPC Layer properties table found herein.

Internal UNL FPC printing shall be completed in the same manner as the vendor’s procedure with the exception being that the UNL-Standard.CTB file should be used as the AutoCAD®.dwg file should contain the respective UNL Layer Properties from the vendor.

## Sheet Size

UNL FPC requires all projects to be delivered on a standard 24”x36” or 30”x42” sheet size.  UNL required cover sheets and title block templates on 24”x36” and 30”x42” sheets are available for download and can be found in the CAD library downloads section.

There may be times when it may become necessary to utilize a larger or alternate sized sheet size for special circumstances.  In the event an alternate sheet size is needed a new cover sheet and title block shall be constructed similarly and with the same attributes as the standard UNL cover sheet and title block.  The alternate sheet size, cover sheet and title block shall be submitted and approved by UNL FPC prior to its use describing the reason to waiver away from the standard sheet size.

When submitting project drawing revisions, sketch sheets or supplemental drawings the standard UNL FPC required sheet size shall be 8.5”x11” or 11”x17”.  UNL required sketch sheets and supplemental drawing title block templates on 8.5”x11” and/or 11”x17” sheets are available for download and can be found in the CAD library downloads section.

## Delivery

Delivery of drawing files whether produced in CAD or BIM shall be delivered in the same format as described herein.  Progress milestones, review submittals, construction documents, revisions and “as-built” documents shall all follow the same delivery process, procedure and requirements as outlined herein these guidelines.

UNL FPC requires all drawing files to be submitted in the most current version of AutoCAD®.  AutoCAD® files shall also be accompanied with a respective .pdf in order to properly view the vendor’s intent of the finished plotted AutoCAD®.dwg file.

When possible any multiple .dwg files shall be zipped into one .zip file and the drawing “pdf’s” shall be combined into one .pdf binder both file names shall follow the file naming nomenclature as described herein.

Follow and complete the Electronic File Quality Assurance Checklist found herein the Reproduction Quality Assurance section.

## Reproduction Quality Assurance

Electronic File Quality Assurance Checklist

CAD drawings delivered at intermediate progress milestones and closeout of a capital project must be accompanied by this checklist and a signed letter on firm letterhead stating that all materials adhere to the standards and guidelines set forth herein the University of Nebraska CAD Standards publication.

FILE FORMAT AND SETUP

□   UNL Electronic File Format

□   UNL Policy on Model Space and Paper Space

□   UNL External Reference (XREFs) Policy

□   UNL Scale, Units, & Tolerances

□   UNL Fonts and Text Styles

□   UNL Dimensioning

□   UNL Details/Block Definitions

□   UNL Title Block/Cover Sheet/Size

□   Current Date Indicated on Drawings

LAYERING

□    UNL Standard Layering

□    AIA and UNL Layer Name Formatting

□    General Rules about Naming and Uses

□    Layer Attributes (Colors, Pens, Linetypes)

Building, CAD, PDF FILE NAME CONVENTIONS

□    Building and Project Identification

□    Discipline Designation Codes

□    Drawing Sheet Numbers

□    Drawing File Name

□    Door Numbering

□    Area Polyline and Square Footage

POLICY ON CAD FILE TRANSLATION

□    Full AutoCAD® Compliance

□    Bound xrefs and images

□    Translation Testing Procedures of Bound xrefs, UNL Layering and Plotting

Deliverables and Closeout

□    Progress Submittal_________ (Phase or %)

□    Construction Documents

□    Supplemental Drawing Revisions

□    “As-Built” Documents

□   AutoCAD®.dwg and .PDF submitted

| Name of Accountable Vendor Representative (Printed) | Signature & Date of Accountable Vendor Representative |
| --- | --- |

# CAD Project Closeout Documentation

## Reference Binding

When submitting drawing plans to UNL FPC all images and external reference files shall be bound into one AutoCAD®.dwg file.  To prevent unintentional updating of archived drawings by later changes to referenced drawings or images, bind the xrefs and images to the final drawing.  Binding an xref or image to a drawing makes the xref a permanent part of the drawing and no longer an externally referenced file.  Bind the entire database of the xref drawing, including all its xref-dependent named objects by using the XREF Bind option.  UNL FPC will not accept the submission of any CAD drawing deliverables which contain unbound external or image reference files.

## Conversions and CAD Translations

BIM, Revit.rvt or other CAD software shall be converted into the latest version of AutoCAD®.dwg files which have no significant loss of drawing information, entities or data from file translation procedures.  It is recommended that a thorough translation/conversion test procedure be conducted before the drawing development phase of the project.  The test shall cover all standards required herein this document.  This will assure early detection of file conversion issues and allow for corrective measures to be taken.  In the event that a non-AutoCAD® source CAD system software does not properly translate certain objects and attributes as required by these guidelines, it will be determined by UNL FPC on a case-by-case basis whether this limitation is deemed acceptable.  It is expected that vendors provide CAD work that are fully compliant with all standards outlined herein.

All DWG files and CAD drawing entities submitted at the end of a project must be able to be manipulated using standard AutoCAD® drafting procedures.  Non-compliance with this policy may result in the rejection of CAD files submitted at project closeout in addition to delayed rendering of final project payment.

## As-Built Documents

Delivery of As-Built Construction drawing files whether produced in CAD or BIM shall be delivered in the same format as described herein these guidelines.

UNL FPC requires all As-Built drawing files to be submitted in the most current version of AutoCAD®.  AutoCAD® files shall also be accompanied with a respective .pdf in order to properly view the intent of the As-Built plotted AutoCAD®.dwg file.

As-built drawings shall include all addendums, change directives, supplemental instructions and any other revisions made to a project that can be identified and indicated on the drawings shall become part of the As-Built file.  Revision clouds and revision identification tags shall not be included as part of the As-built plans and will not be accepted by UNL FPC at project closeout.  The As-built file and any changes shall be provided in the proper UNL layer and layer attributes as well as all other standards described herein.

## Construction Revisions

Construction revisions that impact a project’s drawing set including change directives and supplemental instructions shall be documented and provided electronically as part of the As-Built AutoCAD® file.  Include all AIA documentation, correspondence and discussions regarding said revisions.  During construction or pre-construction these revisions may have been submitted under separate cover and separate title block sheet.  However at closeout of the project these shall become part of the final set of construction As-Built drawings.

## Delivery

All CAD drawings submitted to UNL FPC shall be purged of all un-referenced dimension styles, linetypes, blocks, layers, shapes and text styles.  UNL FPC requires that the UNL FPC CAD standards are strictly followed.  Drawings submitted without bound xrefs, improper layering, door numbering, sheet/file naming, title block/sheet sizes or any other improper parameters set forth herein, are subject to rejection and revision.  The delay of a project or missing project delivery milestones as a result of UNL FPC rejection of an AutoCAD®.dwg will not be acceptable.

## Waiver Procedure

Any request for change or variance in the current University of Nebraska CAD standards or procedures outlined herein shall be made in writing to the UNL FPC CAD manager prior to delivery of any erroneous CAD files.