Compliance:  The design and construction of all electrical distribution systems shall be in complete compliance with the current adopted revision of the National Electric Code (NEC) and the National Electrical Safety Code (ANSI C2).

Utility Plants:  Power is distributed to city and east campus from the corresponding utility plant on each campus.  City campus distribution is divided between a 4160 volt system that feeds most of the core of campus and a 12.5 kv sysem that feeds mainly the perimeter of campus and some of the larger loads in the core.

Primary Service Connections to Building:  The Utility & Energy division within FMPNUCORP shall be consulted for the primary electrical distribution voltage available on Campus.  This information shall be available via the Utility section of the project Program Statement required for each project at UNL.  Extensions of the electrical distribution system, including underground duct, conductors, and electrical manholes, shall be furnished and installed by that Project.    All primary electrical feeders routed inside a building shall be galvanized rigid steel conduit, properly bonded and grounded, and with high voltage warning signs.

Primary electrical feeders within buildings is not allowed.  Pad mounted transformers shall be installed adjacent to each new or remodeled building

Source of Electrical Power:  The electrical distribution system on campus is the required source of electrical power for building projects. Special circumstances and remote locations that incur excessive costs may necessitate the use of service provided by the local utilities. The direct use of local utilities for electrical service shall be accomplished only with the approval of the Director of the Utility & Energy division within FMP. NUCORP

Distribution System:  The electricity on campus is distributed via an underground distribution system.   areas.  Extensions or upgrades of the electrical distribution system are accomplished by installing conductors within underground concrete encased ducts.

New Service:  Provision of a new electrical service to a facility requires extension of the electrical distribution system to the facility from the nearsest distribution switch and installation  of pad mount transformer at each building. Metering with  KYZ output shall be installed at each transformer with conductors to the nearest BSM control panel in 1”conduit  Any new transformer / unit substation that is required must be provided by the project.  Coordinate the purchase of the transformer with NUCORP.  is the  transformer will be owned, operated, and maintained by the Utilities division

Special Requirements:

Extensions of the electrical distribution system shall be included in capital projects, as defined in the Utility Section of the Program Statement.

Provide a single line drawing showing the complete final building distribution system, suitably framed in 24" x 36" size under glass to be mounted in the substation or main switchgear room.

Raceway should be rigid steel conduit, as it passes through the foundation wall, into the service entrance box.

Service Entrance Pull Box:  The primary service shall enter the building through a multi-cell concrete duct envelope in the basement wall and not directly into the unit sub-station.  Provide a No. 12 gauge sheet steel pullbox over the ducts.  Box size shall be determined by the number of ducts to be covered as well as the sizes of cables entering or leaving the box.  Provide a steel barrier to separate the ducts for use of low voltage fire alarm and signal cables.  The box shall have a screw-on cover and shall be painted with two coats of gray enamel paint with "high voltage" stenciled on cover.  The depth of box shall be a minimum of 9 times the diameter of the primary cable.

Future Loads:  Electrical distribution systems/equipment shall be sized and configured to accommodate future loads.

Specific Design Information:  Information about the electrical distribution system and/or its extension to serve a new load shall be obtained From NUCORP. Designer shall provide estimated load to be added duct routing, and most cost effective location of utility service shall be coordinated with NUCORP  Clarifications and further information are available from the NUCORP.