Primary Service Connections to Building:  NUCORP shall be consulted for the primary electrical distribution voltage available on Campus.  This information shall be available via the Utility section of the project Program Statement required for each project at UNL.  Extensions of the electrical distribution system, including underground duct, conductors, and electrical manholes, shall be furnished and installed by that Project.

Primary electrical feeders within buildings is not allowed.  Pad mounted transformers shall be installed adjacent to each new or remodeled building

Source of Electrical Power:  The electrical distribution system on campus is the required source of electrical power for building projects. Special circumstances and remote locations that incur excessive costs may necessitate the use of service provided by the local utilities. The direct use of local utilities for electrical service shall be accomplished only with the approval ofNUCORP

Special Requirements:

Extensions of the electrical distribution system shall be included in capital projects, as defined in the Utility Section of the Program Statement.

Provide a single line drawing showing the complete final building distribution system, suitably framed in 24" x 36" size under glass to be mounted in the substation or main switchgear room.

Electrical meters are required at all buildings. See DG/ Electrical Distribution System for requirements.

Documentation and Submittals: The AE shall review the Project Submittal Requirements.