City Campus Watershed:  Storm water drains into either Salt Creek or Antelope Creek which subsequently drains into Salt Creek.

East Campus Watershed:  Storm water drains into Dead Man’s Run which subsequently drains into Salt Creek.

UNL Drainage Systems:  Both campuses are served by a combination of UNL and City of Lincoln owned and maintained storm drainage systems.  Those owned by UNL, serve only UNL facilities and property, whereas those owned by the City of Lincoln serve a combination of UNL and non UNL facilities.

The design of any new storm systems shall incorporate sustainable and low impact design storm water drainage concepts and principles.

Compliance:  The design and construction of all storm water drainage systems on campus shall be in complete compliance with the current revision of the Standard Specifications for Water and Sewer Main Construction in Nebraska?.  These standards are to be viewed as the “final authority” for establishing the minimum requirements of storm water drainage systems.  They shall also be in full compliance with all applicable requirements of any municipality whose sewer system is located downstream of a particular UNL system.  The requirements of these documents often exceed the minimum requirements referenced above.  When they do, the stricter of the two shall apply.

Storm Water Management Policy:  UNL has adopted a policy to reduce or, at a minimum, maintain the existing peak storm water runoff characteristics of all land and buildings that are or will be under UNL control.  All new construction work and associated storm drainage system work on campus shall be accomplished so as to have, at worst, no impact on any downstream drainage system (i.e. no increase in storm water flow rate under the most extreme condition).  Design shall incorporate sustainable and low impact design storm water drainage concepts and principles.  This requires that a provision be made for storm water detention and/or the use of pervious surfaces as an integral part of new construction projects.  (See Calculations below for detailed requirements.)

Scope of Policy:  This storm water management policy pertains to any Project that will change the peak storm water runoff characteristics, including but not limited to new buildings, renovations of existing buildings, additions to existing buildings, construction of new parking lots, and renovation of existing parking lots. Do we mention Area or just refer to SWPP?

Calculations:  UNL requires that the AE or designer prepare and submit calculations comparing the peak storm water characteristics of the construction site before the construction begins to the peak storm water runoff characteristics of the site after the construction is complete.  The AE must also prepare and submit plans detailing the retention/detention method chosen to reduce the peak storm water runoff to that which existed on the site prior to construction.  Calculations shall be provided to FMP during the project design review process.  These calculations shall be based on the following design criteria:

- The controlled release rate of storm water runoff from a fully developed project site should not exceed the rate of .018 cfs per acre for sites larger than five acres, and 0.9 cfs per acre for sites less than five acres.

- The design rate at which storm water runoff is delivered to a designated storm water storage area should be based on the occurrence of a 100-year storm event after the project site has been fully developed.

- In the event that the existing downstream channel or storm drainage piping system is inadequate to accommodate the required release rate, the allowable release rate shall be reduced to that rate permitted by the capacity of the downstream channel or storm drain system without overflowing of banks or surcharging of piping.

Future Considerations:  All storm drainage piping shall be sized and configured appropriately to serve the ultimate future need for drainage in the geographical area being served.

Manholes:  A manhole shall be provided at each change in direction of the piping system as well as at not greater than 400 feet.

Storm Grates:  All storm grates shall be “bicycle safe” in design and include an integrally cast label stating, “No Dumping – Drains to Stream”.

Surface Drainage:  Positive surface drainage shall be provided such that storm water drains away from all structures.  Surface runoff shall not be allowed to flow across pedestrian walkways, bicycle paths, drives or parking areas in a manner compatible with sustainable and low impact storm water management design.

Specific Design Information:  Information about storm drainage systems and/or their extension/modification to serve new facilities/areas should be obtained via a Program Statement.  Clarifications and further information are available from FMP.