The following schedule pertains to UNL city and east campus buildings (excluding campus housing).  It is the A/E’s responsibility to include this schedule in the construction document plans or specifications.

The coordination schedule for UNL Housing or outstate buildings shall be coordinated with FPC engineering on a project by project basis.

| ITEM | FURNISHED BY | SET BY | POWER WIRING | CONTROL WIRING |
| --- | --- | --- | --- | --- |
| Equipment Motors | MC | MC | EC | UNL BSM |
| Motor Control Centers | EC | EC | EC | UNL BSM |
| Unit Mounted Motor Starters, Contactors, Disconnect Switches, Thermal Overloads And Heaters | MC | MC | EC | UNL BSM |
| Loose Motor Starters, Contactors, Disconnect Switches, Thermal Overloads And Heaters | EC | EC | EC | UNL BSM |
| Pushbutton Stations And Safety Stop Switches – Air Handling Systems And Hydronic Systems | EC | EC | NA | UNL BSM |
| Variable Speed Drives And Associated Safety Disconnects (with appropriate fuses) | UNL BSM | EC | EC | UNL BSM |
| Temporary Heating/Cooling And Connections | GC | MC/EC | EC | MC/EC |
| Thermostats And Terminal Controls – Line Voltage | UNL BSM | EC | EC | EC |
| Chillers and Boilers | MC | MC | EC | MC |
| Computer Room Air Conditioning and Controls | MC | MC | EC | MC |
| DX Split Systems Controls | MC | MC | EC | MC |
| Room Controls Transformer Panels | UNL BSM | EC | EC | UNL BSM |
| Thermostats And Terminal Unit Controls – Low Voltage | UNL BSM | UNL BSM | UNL BSM | UNL BSM |
| Air Terminal Units And Hydronic Reheat Coils | MC | MC | NA | NA |
| Air Terminal Units And Electric Reheat Coils | MC | MC | EC | NA |
| Lab Room and Fume Hood Air Terminal Units | MC | MC | NA | UNL BSM |
| Lab Fume Hood Monitors and/or Controllers | UNL BSM | NA | NA | UNL BSM |
| Air Compressors and Air Dryers | MC | MC | EC | NA |
| Pneumatic Control Air Mains | MC | MC | NA | NA |
| Pneumatic Control Device Terminations | NA | NA | NA | Termination UNL BSM |
| Building Automation System Control Panels | UNL BSM | UNL BSM | EC | UNL BSM |
| Air Handling And Hydronic Systems Controls | UNL BSM | UNL BSM | NA | UNL BSM |
| Air Handling Systems Pressure Sensors | UNL BSM | UNL BSM | NA | UNL BSM |
| Automatic Control Damper Actuators | UNL BSM | UNL BSM | NA | UNL BSM |
| Automatic Control Dampers AHU Economizer | UNL BSM | MC | NA | UNL BSM |
| Air Handling Systems Air Flow Stations | UNL BSM | UNL BSM | NA | UNL BSM |
| Smoke/Fire Dampers | MC | MC | EC | UNL BSM |
| Automatic Flow Control Devices | MC | MC | NA | NA |
| Automatic Control Valves And Actuators | UNL BSM | MC | NA | UNL BSM |
| Hydronic Systems Temperature Sensor Wells | UNL BSM | MC | NA | UNL BSM |
| Hydronic And Steam Systems Pressure Taps | MC | MC | NA | NA |
| Hydronic And Steam Systems Pressure Sensors | UNL BSM | MC | NA | UNL BSM |
| Hydronic Systems Automatic Makeup Systems | MC | MC | EC | UNL BSM |
| Chilled Water Btu Meters | UNL UTIL | MC | EC | UNL BSM |
| Heating Water Flow Meters | UNL UTIL | MC | NA | UNL BSM |
| Steam Condensate Meters | UNL UTIL | MC | EC | UNL BSM |
| Steam Condensate Level Alarm | MC | MC | NA | UNL BSM |
| Sump and Sewage Pump Level Alarm | MC | MC | EC | UNL BSM |
| Water Purification Systems | MC | MC | EC | EC |
| Card Access Conduit | EC | EC | EC | NA |
| Card Access Cabling – Line Voltage | EC | EC | EC | EC |
| Card Access Cabling – Low Voltage | UNL BSM | NA | NA | UNL BSM |
| Card Access Building Controllers | UNL BSM | UNL BSM | EC | UNL BSM |
| Card Access Network Connections | GC | GC | NA | NA |
| Card Access Door Controllers | UNL BSM | UNL BSM | EC | UNL BSM |
| Card Access Door Hardware | GC | GC | EC | UNL BSM |
| Card Access Handicap Door Hardware | GC | GC | EC | UNL BSM |
| Handicap Door Hardware (No Card Access) | GC | GC | EC | EC |
| Card Access Readers | UNL BSM | GC | EC | UNL BSM |
| Card Access Door Position Switch | UNL BSM | GC | EC | UNL BSM |
| Fire Alarm Panels | UNL BSM | UNL BSM | EC | UNL BSM |
| Fire Alarm Communications Circuits | GC | GC | NA | NA |
| Fire Alarm Detectors, Pull Stations, Horns & Strobes | UNL BSM | UNL BSM | EC | UNL BSM |
| Fire Alarm Cabling and Conduit | UNL BSM | UNL BSM | EC | UNL BSM |
| Fire Alarm Relays | UNL BSM | UNL BSM | EC | UNL BSM |
| Room Lighting and Occupancy Sensing | EC | EC | EC | EC |
| Room Occupancy Sensing HVAC Interface | EC | EC | EC | UNL BSM |

Schedule Notes:

GC = General Contractor

MC = Mechanical Contractor

EC = Electrical Contractor

UNL BSM = University of Nebraska – Lincoln, Building Systems Maintenance

UNL UTIL = University of Nebraska – Lincoln, Utilities

NA = Not Applicable