City Campus Watershed:  Storm water drains into either Salt Creek or Antelope Creek which subsequently drains into Salt Creek.

East Campus Watershed:  Storm water drains into Dead Man’s Run which subsequently drains into Salt Creek.

UNL Drainage Systems:  Both city and east campuses are served by a combination of UNL and City of Lincoln owned and maintained storm drainage systems.  Those owned by UNL, serve only UNL facilities and property, whereas those owned by the City of Lincoln serve a combination of UNL and non UNL facilities.

Compliance:  The design and construction of all storm water conveyance systems on City and East campuses shall be in complete compliance with the current revision of the City of Lincoln Department of Public Works – Drainage Criteria Manual found here: http://lincoln.ne.gov/city/pworks/watrshed/require/drainage/

NPDES Storm Water Management Plan:   UNLs SMS4 NPDES Permit requires reducing water quality impacts resulting from post-construction runoff through incorporation of permanent post-construction Best Management Practices (BMPs). All projects must try, to the best extent possible, to limit disruption of natural water hydrology by reducing impervious cover, increasing on-site infiltration, and reducing or eliminating contaminants from storm water runoff. All new construction work and associated storm drainage system work on campus shall minimize impact on any downstream drainage system.   Design shall incorporate sustainable and Low Impact Design (LID) storm water drainage concepts and principles at the extent feasible.

Scope of Plan:  This storm water management plan pertains to any project including but not limited to new buildings, renovations of existing buildings, additions to existing buildings, construction of new parking lots, and renovation of existing parking lots.

Calculations:  UNL requires that the Architect/Engineer (A/E) prepare and submit calculations comparing the peak storm water characteristics of the construction site before the construction begins to the peak storm water runoff characteristics of the site after the construction is complete.  The A/E must also prepare and submit plans detailing the Low Impact Development method chosen to control storm water quality and quantity.  Calculations shall be provided to FMP during the project design review process.

Future Considerations:  All storm drainage piping shall be sized and configured appropriately to serve the ultimate future need for drainage in the geographical area being served.

Manholes:  A manhole shall be provided at each change in direction of the piping system as well as at not greater than 400 feet.

Storm Grates:  All storm grates shall be “bicycle safe” in design and include an integrally cast label stating, “No Dumping – Drains to Stream”.

Surface Drainage:  Positive surface drainage shall be provided such that storm water drains away from all structures.  Surface runoff shall not be allowed to flow across pedestrian walkways, bicycle paths, drives or parking areas in a manner compatible with sustainable and low impact storm water management design.