## ahus
AIR HANDLING UNIT SCHEDULE
EQUIPMENT MARK: | AHU-1
UNIT SERVES:
UNIT TYPE:
Draw Thru / Blow Thru | BLOW THRU
Type: | VARIABLE VOLUME
MANUFACTURER AND MODEL:
Motor VOLTAGE / PHASE / HERTZ | 480/3/60
UNIT COMPONENTS IN DIRECTION OF AIRFLOW: | RETURN PLENUM
RETURN FAN
ECONOMIZER SECTION
AIR BLENDER
FILTER SECTION
PREHEAT COIL
ACCESS SECTION
SUPPLY FAN SECTION
COOLING COIL SECTION
SUPPLY AIR PLENUM
RETURN PLENUM:
Return Air Damper - Max. Airflow (CFM) | 80000
Remarks:
FAN SECTION: | RF-1
Type | FAN ARRAY
Rows x Columns | 5 X 1
Airflow [CFM] | 80000
External Static Pressure [in w.g.] | 3.80"
Total Static Pressure [in w.g.] | 3.80"
Fan BHP / RPM per Fan | 12.9 / 1159
Motor HP /RPM per Fan | 15 / 1200
Motor VOLTAGE / PHASE / HERTZ | 480/3/60
Fan Wheel: Size/Type/Motor | 33" / DIRECT-DRIVE / TEAO
Remarks: | BACKDRAFT DAMPER AT EACH FAN
ECONOMIZER:
Relief Air Damper - Max. Airflow (CFM) | 80000
Outside Air Damper - Min. Airflow (CFM) - Normal | 20000
Outside Air Damper - Min. Airflow (CFM) - Game Day | 40000
Outside Air Damper - Max. Airflow (CFM) | 80000
Remarks:
PRE-FILTER:
Media Type: | 4" PLEATED 30% EFFICIENT ANGLED
Airflow (CFM) | 80000
Face Velocity[FPM]: | 450
Filter Air Pressure Drop [in w.g.] | 0.5
Remarks: | AIR PRESSURE DROP FOR "MID LIFE" FILTERS
FINAL FILTER:
Media Type: | 12" CARTRIDGE FILTER, MERV 11
Airflow (CFM) | 80000
Face Velocity[FPM]: | 450
Filter Air Pressure Drop [in w.g.] | 0.5
Remarks: | AIR PRESSURE DROP FOR "MID LIFE" FILTERS
PREHEAT COIL: | PHC-1
Turbulators | NO
Coil Rows / Fins per Inch: | 2 / 10
Coil Size / Wall Thickness / Material: | 5/8" / 0.025" / COPPER WITH ALUM FINS
Coil Face Area [sq ft] | 179
Face Velocity [FPM] | 447
Medium: | 40% PROPYLENE GLYCOL
Airflow [CFM] | 80000
Coil Capacity [MBH] | 3408.6
Air Temperature EAT / LAT [Deg F] | 21/60
Air Pressure Drop [in w.g.] | 0.1
Water Flowrate [gpm] | 133.3
Entering Water Temp. [Deg F] | 140
Leaving Water Temp. [Deg F] | 85
Water Pressure Drop [ft w.g.] | 5.05
FAN SECTION: | SF-1
Type | FAN ARRAY
Rows x Columns | 5 X 1
Airflow [CFM] | 80000
External Static Pressure [in w.g.] | 4.00"
Total Static Pressure [in w.g.] | 8.00"
Fan BHP / RPM per Fan | 27.27 / 1745
Motor HP /RPM per Fan | 40 /1800
Motor VOLTAGE / PHASE / HERTZ | 480/3/60
Fan Wheel: Size/Type/Motor | 30" / DIRECT-DRIVE / TEAO
Remarks: | BACKDRAFT DAMPER AT EACH FAN
CHILLED WATER COIL: | CC-1
Turbulators | NO
Coil Rows / Fins per Inch: | 10 / 10
Coil Size / Wall Thickness / Material: | 5/8" / 0.025" / COPPER WITH ALUM FINS
Coil Face Area [sq ft] | 177
Face Velocity [FPM] | 454
Medium: | 25% PROPYLENE GLYCOL
Airflow [CFM] | 80000
Coil Total Capacity {MBH} | 4979
Coil Sensible Capacity {MBH} | 3238
Air Temperature EDB / EWB [Deg F] | 89 / 72
Air Temperature LDB / LWB [Deg F] | 53 / 53
Air Pressure Drop [in w.g.] | 1.02
Water Flowrate [gpm] | 931.5
Entering Water Temp. [Deg F] | 47
Leaving Water Temp. [Deg F] | 58
Water Pressure Drop [ft w.g.] | 23.2
REHEAT COIL: | RHC-1
Turbulators | NO
Coil Rows / Fins per Inch: | 2 / 10
Coil Size / Wall Thickness / Material: | 5/8" / 0.025" / COPPER WITH ALUM FINS
Coil Face Area [sq ft] | 179
Face Velocity [FPM] | 447
Medium: | 40% PROPYLENE GLYCOL
Airflow [CFM] | 80000
Coil Capacity [MBH] | 3408.6
Air Temperature EAT / LAT [Deg F] | 21/60
Air Pressure Drop [in w.g.] | 0.1
Water Flowrate [gpm] | 133.3
Entering Water Temp. [Deg F] | 140
Leaving Water Temp. [Deg F] | 85
Water Pressure Drop [ft w.g.] | 5.05
Sound Power (Discharge/Radiated)
1st Octave Band | 87 / 84
2nd Octave Band | 84 / 76
3rd Octave Band | 94 / 78
4th Octave Band | 88 / 76
5th Octave Band | 81 / 64
6th Octave Band | 80 / 58
7th Octave Band | 78 / 54
8th Octave Band | 72 / 47
ADDITIONAL REMARKS: | 1,2,3,4,5,6
NOTES:
1) ALL COIL PERFORMANCE DATA SUBMITTALS MUST BE COMPUTER GENERATED - NO EXCEPTIONS.
2) ALL SOUND PERFORMANCE DATA SUBMITTALS MUST BE COMPUTER GENERATED - NO EXCEPTIONS.
3) PROVIDE HINGED, GASKETED ACCESS DOORS WITH VENT-LOCK HANDLES . ALL ACCESS DOORS SHALL HAVE VIEWING WINDOWS.
4) ENERGY EFFICIENT, INVERTER DUTY MOTORS WITH BUILT-IN SHAFT GROUNDING OR SHAFT GROUNDING KITS
5) PROVIDE BACKDRAFT DAMPERS ON FANS
6) PROVIDE FACTORY MOUNTED OA, RELIEF AND RETURN AIR DAMPERS ON ALL AIR HANDLING UNITS. DAMPERS SHALL BE TAMCO MODEL 1500 FOR RELIEF AND RETURN AIR DAMPERS AND OUTSIDE AIR DAMPERS ARE TO BE TAMCO MODEL 9000 SC - NO EQUIVALENT
7) PROVIDE AIR GAP BETWEEN PRE AND FINAL FILTERS FOR DIFFERENTIAL PRESSURE MONITORING FOR PRE AND FINAL FILTERS INDIVIDUALLY. THIS MEANS CANNOT HAVE PRE FILTERS THAT SNAP DIRECTLY TO FINAL FILTERS.