PART 1 – LINE SPECIFICATIONS

- GENERAL

- The following sections detail line specifications for piping and equipment located in Husker Energy & Power Utility Plants.

- LINE MATRIX

| LINE SPEC | DESCRIPTION | APPLICABLE LOCATIONS |
| --- | --- | --- |
| CC-HPS | City Campus High Pressure Steam | CCUP |
| CC-MPS | City Campus Medium Pressure Steam | CCUP |
| CC-LPS | City Campus Low Pressure Steam | CCUP |
| CC-FWH | City Campus High Pressure Feedwater | CCUP |
| CC-FWM | City Campus Medium Pressure Feedwater | CCUP |
| CC-HPB | City Campus High Pressure Boiler Attachments | CCUP |
| CC-MPB | City Campus Medium Pressure Boiler Attachments | CCUP |
| EC-MPS | East Campus Medium Pressure Steam | ECUP |
| EC-LPS | East Campus Low Pressure Steam | ECUP |
| EC-FWM | East Campus Medium Pressure Feedwater | ECUP |
| EC-MPB | East Campus Medium Pressure Boiler Attachments | ECUP |
| UP-FWSR | City Campus Feedwater Suction and Recirculation | CCUP, ECUP |
| UP-DAW | Deaerator Makeup Water | CCUP, ECUP |
| UP-CHW | Chilled Water Supply and Return | CCUP, CTES, ECUP, ETES |
| UP-TW | Tower Water Supply and Return | CCUP, ECUP, ETES |

LINE REQUIREMENTS

Specification:	CC-HPS

Location:	City Campus Utility Plant

Working Fluid:	High Pressure Superheated Steam

Design Conditions:	750 PSIG, 900°F

Normal Operating Conditions:	600 PSIG, 825°F

General Material Specification:	1-1/4CR, 1/2MO Steel (P4)

Pipe Material:	A335-P11

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A182-F11, CL3000, Socket Weld Ends.

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WP11, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound suitable for high temperature service. Flexitallic style CGI with Thermiculite 835 filler or equivalent.

Hardware:	A193 CL2 Gr B16 Bolts with A194 CL2 Gr 7 Nuts

Insulation Color:	None; embossed aluminum.

Insulation Thickness Selection Conditions:	130°F max surface temp; 850°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	Socket Weld

Material:	A182-F11 Forged Steel

Specification:	ASME B16.34

Ball:	Full port, metal seated, A182-F11, rated for ASME B16.34. ValvTechnologies CL900 V1-1 or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge, API Trim 5. Vogt SW12321FHF, Velan W-2054B-05-TS, Bonney Forge HL19FSW or equivalent.

Globe:	Bolted bonnet, OS&Y, API Trim 5. Vogt SW12351FHF, Velan W-2074B-05TS, Bonney Forge HL39FSW or equivalent.

Strainer:	Keckley SB-C6 (1500 lb) or equivalent, 1/32” screen perforation.

Check:	Not permitted

Valves, Larger than 2”:

Pressure Class:	600

End Connection:	Butt Weld, bore to match jointing pipe

Material:	A217-WC6 Cast Steel

Ball:	Not permitted

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 5. Crane 76-1/2XUF6, Powell 6003ID5G, Velan B-2064C-05TS or equivalent.

Butterfly:	Not permitted

Globe:	Bolted Bonnet, OS&Y, API Trim 5. Crane 171-1/2XUF6, Powell 6031ID5G, Velan B-2074C-05TS or equivalent.

Check:	Boiler Non-Return Valves Only. ≤ 10 PSID differential pressure at rated flow conditions with minimum 10:1 turndown. Requires UNL approval.

Specialties:	Require separate approval by HEP and FPCP Engineering (Boiler specialties including blowoff, continuous blowdown, gage valves, safety valves; control valves; desuperheaters).

Special Notes:	Equipment within ASME Code Boundary (Boiler 1 steam outlet) require MTRs. Welding within ASME Code Boundary requires R-stamp contractor. R-Stamp contractors to procure materials for welding within ASME Code Boundaries to facilitate inspection.

LINE REQUIREMENTS

Specification:	CC-MPS

Location:	City Campus Utility Plant and Distribution System

Working Fluid:	Medium Pressure Superheated Steam

Design Conditions:	350 PSIG, 600°F

Normal Operating Conditions:	250 PSIG, 500°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL2000 or 3000, NPT or Socket Weld Ends.

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	International Orange

Insulation Thickness Selection Conditions:	130°F max surface temp; 500°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	Socket Weld or NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	Full port, metal seated, A105, rated for ASME B16.34. ValvTechnologies CL300 V1-2 or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge, API Trim 5. Vogt (SW)12111FHF, Velan (S/W)-2054B-05-TS, Bonney Forge HL12(SW/T) or equivalent.

Globe:	Bolted bonnet, OS&Y, API Trim 5. Vogt (SW)12141FHF, Velan (S/W)-2074B-02TS, Bonney Forge HL32(SW/T) or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 3/64” screen perforation.

Check:	Bolted bonnet, swing check. Velan (S/W)-2114B-02TY, Vogt S701, Bonney Forged HL61(SW/T) or equivalent

Valves, Larger than 2”:

Pressure Class:	300

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Not permitted

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 33XUF, Powell 3003FC8G, Velan F-1064C-02TY or equivalent.

Butterfly:	Conforming to ASME B16.34. Triple-offset high-performance butterfly valve, metal seated, CL300 double-flanged. Emerson Vanessa series 30000 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 5. Crane 151XUF, Powell 3031FC8G, Velan F-1074C-02TY or equivalent.

Check:	Boiler Non-Return Valves Only. ≤ 10 PSID differential pressure at rated flow conditions with minimum 10:1 turndown. Requires UNL approval.

Specialties:	Require separate approval by HEP and FPCP Engineering (Boiler specialties including blowoff, continuous blowdown, gage valves, safety valves; control valves; desuperheaters).

Special Notes:	Equipment within ASME Code Boundary (Boiler 2/7/8 steam outlets) require MTRs. Welding within ASME Code Boundary requires R-stamp contractor. R-Stamp contractors to procure materials for welding within ASME Code Boundaries to facilitate inspection.

LINE REQUIREMENTS

Specification:	CC-LPS

Location:	City Campus Utility Plant and Distribution System

Working Fluid:	Low Pressure Superheated Steam

Design Conditions:	42 PSIG, 450°F

Normal Operating Conditions:	33 PSIG, 325°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, NPT Ends.

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Light blue

Insulation Thickness Selection Conditions:	125°F max surface temp; 325°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	3-piece body, full port, 316SS ball and stem, PEEK seats, lockable stem extension. Sharpe 99-46PG-TE-L or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt 12111, Velan S-2054B-02TY, Bonney Forge HL11T or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt 12141, Velan S-2074B-02TY, Bonney Forge HL31T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 3/64” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forge HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	150

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Standard port, 316 SS ball & stem, 2-1/4” stem extension, PEEK seats and graphite packing. Apollo 88B-140-04-38 Series or equivalent.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 47XUF, Powell 1503FC8G, Velan F-0064C-02TY.

Butterfly:	Conforming to ASME B16.34, A216-WCC. Triple-offset high-performance butterfly valve, metal seated, CL150. Emerson Vanessa series 30000 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 5. Crane 143XUF, Powell 1531FC8G, Velan F-0074C-02TY or equivalent.

Check:	Requires separate approval by HEP and FPCP Engineering.

Specialties:	Require separate approval by HEP and FPCP Engineering (safety valves; control valves; desuperheaters).

LINE REQUIREMENTS

Specification:	CC-FWH

Location:	City Campus Utility Plant

Working Fluid:	High Pressure Boiler Feedwater Supply

Design Conditions:	1000 PSIG, 450°F.

Normal Operating Conditions:	920 PSIG, 231°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, SW Ends (except for unions which shall be NPT)

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Ford blue

Insulation Thickness Selection Conditions:	125°F max surface temp; 231°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	SW

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	Not permitted.

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt SW12111, Velan W-2054B-02TY, Bonney Forge HL11SW or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt SW12141, Velan W-2074B-02TY, Bonney Forge HL31SW or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bolted bonnet, swing check. Velan W-2114B-02TY, Vogt S701, Bonney Forge HL61SW or equivalent

Valves, Larger than 2”:

Pressure Class:	600

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Requires separate approval by HEP and FPCP Engineering.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 76XUF, Powell 6003FC8G, Velan F-2064C-02TY.

Butterfly:	Conforming to ASME B16.34, A216-WCC. Triple-offset high-performance butterfly valve, metal seated, CL600. Emerson Vanessa series 30000 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 8. Crane 171XUF, Powell 6031FC8G, Velan F-2074C-02TY or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 175XUF, Powell 6061FC8G, Velan F-2114C-02TY or equivalent.

Specialties:	Require separate approval by HEP and FPCP Engineering (safety valves; control valves, flow orifices).

LINE REQUIREMENTS

Specification:	CC-FWM

Location:	City Campus Utility Plant

Working Fluid:	Medium Pressure Boiler Feedwater Supply

Design Conditions:	500 PSIG, 450°F.

Normal Operating Conditions:	310 PSIG, 231°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, SW Ends (except for unions which shall be NPT)

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Ford blue

Insulation Thickness Selection Conditions:	125°F max surface temp; 231°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	SW or NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	3-piece body, full port, 316SS ball and stem, PEEK seats and graphite packing, lockable stem extension. Sharpe 99-46PG-TE-L or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt (SW)12111, Velan (S/W)-2054B-02TY, Bonney Forge HL11(SW/T) or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt (SW)12141, Velan (S/W)-2074B-02TY, Bonney Forge HL31(SW/T) or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bolted bonnet, swing check. Velan (S/W)-2114B-02TY, Vogt S701, Bonney Forge HL61(SW/T) or equivalent

Valves, Larger than 2”:

Pressure Class:	300

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Requires separate approval by HEP and FPCP Engineering.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 33XUF, Powell 3003FC8G, Velan F-1064C-02TY.

Butterfly:	Conforming to ASME B16.34, A216-WCC. Triple-offset high-performance butterfly valve, metal seated, CL300. Emerson Vanessa series 30000 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 8. Crane 151XUF, Powell 3031FC8G, Velan F-1074C-02TY or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 159XUF, Powell 3061FC8G, Velan F-1114C-02TY or equivalent.

Specialties:	Require separate approval by HEP and FPCP Engineering (safety valves; control valves, flow orifices).

LINE REQUIREMENTS

Specification:	UP-FWSR

Location:	City Campus Utility Plant, East Campus Utility Plant

Working Fluid:	Boiler Feedwater Suction and Recirculation

Design Conditions:	85 PSIG, 450°F.

Normal Operating Conditions:	25 PSIG, 231°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, SW Ends (except for unions which shall be NPT)

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Ford blue

Insulation Thickness Selection Conditions:	125°F max surface temp; 231°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	3-piece body, full port, 316SS ball and stem, PEEK seats and graphite packing, lockable stem extension. Sharpe 99-46PG-TE-L or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt 12111, Velan S-2054B-02TY, Bonney Forge HL11T or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt 12141, Velan S-2074B-02TY, Bonney Forge HL31T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forge HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	150

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Requires separate approval by HEP and FPCP Engineering.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 33XUF, Powell 3003FC8G, Velan F-1064C-02TY.

Butterfly:	Double-offset high-performance butterfly valve; carbon steel body with stainless stem and disc, RTFE seats, lug-style body. Crane Flowseal 1LA-12DPGG, Jamesbury 815L, Pratt HP2-150-xxx-6663G, DeZURIK BHP L1 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 8. Crane 143XUF, Powell 1531FC8G, Velan F-0074C-02TY or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 147XUF, Powell 1561FC8G, Velan F-0114C-02TY or equivalent.

Specialties:	Require separate approval by HEP and FPCP Engineering (suction strainers).

LINE REQUIREMENTS

Specification:	CC-HPB

Location:	City Campus Utility Plant Boiler 1 Attachments within ASME B31.1 Code Boundary (upstream of superheater)

Working Fluid:	High Pressure Saturated Boiler Water/Steam

Design Conditions:	750 PSIG, 650°F

Normal Operating Conditions:	625 PSIG, 493°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, SW Ends (except for unions which shall be NPT)

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Black

Insulation Thickness Selection Conditions:	125°F max surface temp; 231°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	Not permitted

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt 12111, Velan S-2054B-02TY, Bonney Forge HL11T or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt 12141, Velan S-2074B-02TY, Bonney Forge HL31T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forge HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	600

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Requires separate approval by HEP and FPCP Engineering.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 76XUF, Powell 6003FC8G, Velan F-2064C-02TY.

Butterfly:	Not permitted.

Globe:	Bolted Bonnet, OS&Y, API Trim 8. Crane 171XUF, Powell 6031FC8G, Velan F-2074C-02TY or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 175XUF, Powell 6061FC8G, Velan F-2114C-02TY or equivalent.

Specialties:	Require separate approval by HEP and FPCP Engineering (boiler specialties – blowdown, gage valves, etc.).

Special Notes:	Equipment within ASME Code Boundary require MTRs. Welding within ASME Code Boundary requires R-stamp contractor. R-Stamp contractors to procure materials for welding within ASME Code Boundaries to facilitate inspection.

LINE REQUIREMENTS

Specification:	CC-MPB

Location:	City Campus Utility Plant Boiler 2/7/8 Attachments within ASME B31.1 Code Boundary (upstream of superheater)

Working Fluid:	Medium Pressure Saturated Boiler Water/Steam

Design Conditions:	350 PSIG, 650°F

Normal Operating Conditions:	270 PSIG, 413°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, SW Ends (except for unions which shall be NPT)

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Black

Insulation Thickness Selection Conditions:	125°F max surface temp; 231°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	Not permitted

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt 12111, Velan S-2054B-02TY, Bonney Forge HL11T or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt 12141, Velan S-2074B-02TY, Bonney Forge HL31T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forge HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	300

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Requires separate approval by HEP and FPCP Engineering.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 33XUF, Powell 3003FC8G, Velan F-1064C-02TY.

Butterfly:	Not permitted.

Globe:	Bolted Bonnet, OS&Y, API Trim 8. Crane 151XUF, Powell 3031FC8G, Velan F-1074C-02TY or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 159XUF, Powell 3061FC8G, Velan F-1114C-02TY or equivalent.

Specialties:	Require separate approval by HEP and FPCP Engineering (boiler specialties – blowdown, gage valves, etc.).

Special Notes:	Equipment within ASME Code Boundary require MTRs. Welding within ASME Code Boundary requires R-stamp contractor. R-Stamp contractors to procure materials for welding within ASME Code Boundaries to facilitate inspection.

LINE REQUIREMENTS

Specification:	EC-MPS

Location:	East Campus Utility Plant and Distribution System

Working Fluid:	Medium Pressure Saturated Steam

Design Conditions:	175 PSIG, 450°F

Normal Operating Conditions:	125 PSIG, 353°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL2000 or 3000, NPT or Socket Weld Ends.

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	International Orange

Insulation Thickness Selection Conditions:	130°F max surface temp; 353°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	3-piece body, full port, 316SS ball and stem, PEEK seats, lockable stem extension. Sharpe 99-46PG-TE-L or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge, API Trim 5. Vogt 12111FHF, Velan S-2054B-05-TS, Bonney Forge HL12T or equivalent.

Globe:	Bolted bonnet, OS&Y, API Trim 5. Vogt 12141FHF, Velan S-2074B-02TS, Bonney Forge HL32T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 3/64” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forged HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	300

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Standard port, 316 SS ball & stem, 2-1/4” stem extension, PEEK seats and graphite packing. Apollo 88B-140-04-38 Series or equivalent.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 33XUF, Powell 3003FC8G, Velan F-1064C-02TY or equivalent.

Butterfly:	Conforming to ASME B16.34. Triple-offset high-performance butterfly valve, metal seated, CL300 double-flanged. Emerson Vanessa series 30000 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 5. Crane 151XUF, Powell 3031FC8G, Velan F-1074C-02TY or equivalent.

Check:	Boiler Non-Return Valves Only. ≤ 10 PSID differential pressure at rated flow conditions with minimum 10:1 turndown. Requires UNL approval.

Specialties:	Require separate approval by HEP and FPCP Engineering (Boiler specialties including blowoff, continuous blowdown, gage valves, safety valves; control valves; desuperheaters).

Special Notes:	Equipment within ASME Code Boundary (Boiler 4/5/6/7 steam outlets) require MTRs. Welding within ASME Code Boundary requires R-stamp contractor. R-Stamp contractors to procure materials for welding within ASME Code Boundaries to facilitate inspection.

LINE REQUIREMENTS

Specification:	EC-LPS

Location:	East Campus Utility Plant and Distribution System

Working Fluid:	Low Pressure Saturated Steam

Design Conditions:	90 PSIG, 450°F

Normal Operating Conditions:	60 PSIG, 307°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL2000 or 3000, NPT or Socket Weld Ends.

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Light Blue

Insulation Thickness Selection Conditions:	130°F max surface temp; 353°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	3-piece body, full port, 316SS ball and stem, PEEK seats, lockable stem extension. Sharpe 99-46PG-TE-L or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge, API Trim 5. Vogt 12111FHF, Velan S-2054B-05-TS, Bonney Forge HL12T or equivalent.

Globe:	Bolted bonnet, OS&Y, API Trim 5. Vogt 12141FHF, Velan S-2074B-02TS, Bonney Forge HL32T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 3/64” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forged HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	150

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Standard port, 316 SS ball & stem, 2-1/4” stem extension, PEEK seats and graphite packing. Apollo 88B-140-04-38 Series or equivalent.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 47XUF, Powell 1503FC8G, Velan F-0064C-02TY or equivalent.

Butterfly:	Conforming to ASME B16.34, A216-WCC. Triple-offset high-performance butterfly valve, metal seated, CL150 double-flanged. Emerson Vanessa series 30000 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 5. Crane 143XUF, Powell 1531FC8G, Velan F-0074C-02TY or equivalent.

Check:	Requires separate approval by HEP and FPCP Engineering.

Specialties:	Require separate approval by HEP and FPCP Engineering (safety valves; control valves).

LINE REQUIREMENTS

Specification:	EC-FWM

Location:	East Campus Utility Plant

Working Fluid:	Medium Pressure Boiler Feedwater Supply

Design Conditions:	313 PSIG, 300°F.

Normal Operating Conditions:	180 PSIG, 231°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, SW Ends (except for unions which shall be NPT)

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Ford blue

Insulation Thickness Selection Conditions:	125°F max surface temp; 231°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	3-piece body, full port, 316SS ball and stem, PEEK seats and graphite packing, lockable stem extension. Sharpe 99-46PG-TE-L or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt 12111, Velan S-2054B-02TY, Bonney Forge HL11T or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt 12141, Velan S-2074B-02TY, Bonney Forge HL31T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forge HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	300

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Requires separate approval by HEP and FPCP Engineering.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 33XUF, Powell 3003FC8G, Velan F-1064C-02TY.

Butterfly:	Conforming to ASME B16.34, A216-WCC. Triple-offset high-performance butterfly valve, metal seated, CL300. Emerson Vanessa series 30000 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 8. Crane 151XUF, Powell 3031FC8G, Velan F-1074C-02TY or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 159XUF, Powell 3061FC8G, Velan F-1114C-02TY or equivalent.

Specialties:	Require separate approval by HEP and FPCP Engineering (safety valves; control valves, flow orifices).

LINE REQUIREMENTS

Specification:	EC-MPB

Location:	East Campus Utility Plant Boiler 4/5/6/7 Attachments within ASME B31.1 Code Boundary

Working Fluid:	Medium Pressure Saturated Boiler Water/Steam

Design Conditions:	250 PSIG, 650°F

Normal Operating Conditions:	145 PSIG, 363°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A106 GrB

Pipe Thickness:	≤ 2” NPS	Schedule 80

≥ 2-1/2” NPS	Schedule 40

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, SW Ends (except for unions which shall be NPT)

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Black

Insulation Thickness Selection Conditions:	125°F max surface temp; 231°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	Not permitted

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt 12111, Velan S-2054B-02TY, Bonney Forge HL11T or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt 12141, Velan S-2074B-02TY, Bonney Forge HL31T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forge HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	300

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Requires separate approval by HEP and FPCP Engineering.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 33XUF, Powell 3003FC8G, Velan F-1064C-02TY.

Butterfly:	Not permitted.

Globe:	Bolted Bonnet, OS&Y, API Trim 8. Crane 151XUF, Powell 3031FC8G, Velan F-1074C-02TY or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 159XUF, Powell 3061FC8G, Velan F-1114C-02TY or equivalent.

Specialties:	Require separate approval by HEP and FPCP Engineering (boiler specialties – blowdown, gage valves, etc.).

Special Notes:	Equipment within ASME Code Boundary require MTRs. Welding within ASME Code Boundary requires R-stamp contractor. R-Stamp contractors to procure materials for welding within ASME Code Boundaries to facilitate inspection.

LINE REQUIREMENTS

Specification:	UP-DAW

Location:	City Campus Utility Plant, East Campus Utility Plant

Working Fluid:	Deaerator Makeup Water (Cold Condensate)

Design Conditions:	100 PSIG, 250°F

Normal Operating Conditions:	50 PSIG, 180°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	A53 GrB

Pipe Thickness:	All sizes	Schedule 80

Fittings:	≤ 2” NPS	Conform to ASME B16.11. A105, CL3000, NPT

≥ 2-1/2” NPS	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Spiral-wound. Garlock FLEXSEAL RW or equivalent.

Hardware:	A193 CL2 Gr B7 Bolts with A194 Gr 2H Nuts

Insulation Color:	Morning Dew

Insulation Thickness Selection Conditions:	125°F max surface temp; 231°F Process temp; 0.5 MPH wind speed; 85°F ambient temperature.

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	Bronze, 2-piece, full port, 316 SS Ball & Stem, PTFE seats, stem extension. Apollo 77-140-50 or equivalent.

Gate:	Bolted bonnet, OS&Y, solid wedge. Vogt 12111, Velan S-2054B-02TY, Bonney Forge HL11T or equivalent.

Globe:	Bolted bonnet, OS&Y. Vogt 12141, Velan S-2074B-02TY, Bonney Forge HL31T or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bolted bonnet, swing check. Velan S-2114B-02TY, Vogt S701, Bonney Forge HL61T or equivalent

Valves, Larger than 2”:

Pressure Class:	150

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Standard port, 316 SS ball & stem, 2-1/4” stem extension, PEEK seats and graphite packing. Apollo 88B-140-04-38 Series or equivalent.

Gate:	Bolted bonnet, OS&Y, flexible wedge, API Trim 8. Crane 47XUF, Powell 1503FC8G, Velan F-0064C-02TY.

Butterfly:	Double-offset high-performance butterfly valve; carbon steel body with stainless stem and disc, RTFE seats. Crane Flowseal xx-1LA-12DPGG, Jamesbury 815L, Pratt HP2-150-xxx-663G, DeZURIK BHP L1 or equivalent.

Globe:	Bolted Bonnet, OS&Y, API Trim 8. Crane 143XUF, Powell 1531FC8G, Velan F-0074C-02TY or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 147XUF, Powell 1561FC8G, Velan F-2014C-02TY or equivalent.

Specialties:	Require separate approval by HEP and FPCP Engineering (control valves).

LINE REQUIREMENTS

Specification:	UP-CHW

Location:	City Campus Utility Plant, City Thermal Energy Storage, East Campus Utility Plant, East Thermal Energy Storage

Working Fluid:	Treated Chilled Water Supply and Return

Design Conditions:	200 PSIG, 100°F

Normal Operating Conditions:	100 PSIG, 40°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	2” NPS and smaller	A106 GrB

2-1/2” NPS and larger	A53 GrB

Pipe Thickness:	2” NPS and smaller	Schedule XS

2-1/2” NPS and larger	Schedule STD

Fittings:	2” NPS and smaller	Conform to ASME B16.11. A105, CL3000, NPT

2-1/2” NPS and larger	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Garlock 3500 series or equivalent. 1/16” thick for pipe sizes 10” and smaller; 1/8” thick for pipe sizes 12” and larger

Hardware:	A307 GrB bolts with A563 GrA nuts

Insulation Color:	Hastings Green

Insulation Thickness Selection Conditions:	Condensation control; 38°F process temperature; 95°F Ambient Temp; 77°F dew point

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	Bronze body, threaded, 316 SS ball and steam, full port, Teflon seat rings, blowout-proof stem, two piece construction, 600 psi WOG, 150 psi SWP, Apollo 77-140 series or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bronze body, bronze trim, bronze rotating swing disc, threaded ends.

Valves, Larger than 2”:

Pressure Class:	150

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Standard port, 316 SS ball & stem, 2-1/4” stem extension, Teflon seats. Apollo 88B-140-04-35 Series or equivalent.

Gate:	Bolted bonnet, OS&Y, rising stem, solid wedge with bronze seat rings, flanged ends, class 125 iron body with bronze trim, MSS SP-70. Add valve stem extensions to all valves that will be installed in insulated piping systems.

Butterfly:	Lug-style double-offset high-performance butterfly valve for double dead-end service; carbon steel body with stainless stem and disc, RTFE seats. Crane Flowseal xx-1LA-12DPGG, Jamesbury 815L, Pratt HP2-150-xxx-663G, DeZURIK BHP L1 or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 147XUF, Powell 1561FC8G, Velan F-2014C-02TY or equivalent.

Non-Slam Check:	Carbon steel body, double-flanged retainerless spring-loaded check valve, EPDM seat (No Buna-N).

Expansion Joints:	EPDM Tube with EPDM cover. Primed and painted carbon steel split retainer ring. Where required, control rods, gussets, and compressions sleeves shall be stainless steel.

Special Notes:	No Buna-N materials.

LINE REQUIREMENTS

Specification:	UP-TW

Location:	City Campus Utility Plant, East Campus Utility Plant, East Thermal Energy Storage

Working Fluid:	Treated Tower Water Supply and Return

Design Conditions:	150 PSIG, 150°F

Normal Operating Conditions:	50 PSIG, 95°F

General Material Specification:	Carbon Steel (P1)

Pipe Material:	2” NPS and smaller	A106 GrB

2-1/2” NPS and larger	A53 GrB

Pipe Thickness:	2” NPS and smaller	Schedule XS

2-1/2” NPS and larger	Schedule STD

Fittings:	2” NPS and smaller	Conform to ASME B16.11. A105, CL3000, NPT

2-1/2” NPS and larger	Conform to ASME B16.9. A234-WPB, Butt Weld Ends, bored to match jointing pipe.

Gaskets:	Garlock 3500 series or equivalent. 1/16” thick for pipe sizes 10” and smaller; 1/8” thick for pipe sizes 12” and larger

Hardware:	A307 GrB bolts with A563 GrA nuts

Paint Color:	Hastings Green

Insulation Thickness Selection Conditions:	None

Valves, 2” and Smaller:

Pressure Class:	800

End Connection:	NPT

Material:	A105 Forged Steel

Specification:	ASME B16.34

Ball:	Bronze body, threaded, 316 SS ball and steam, full port, Teflon seat rings, blowout-proof stem, two piece construction, 600 psi WOG, 150 psi SWP, Apollo 77-140 series or equivalent.

Strainer:	Keckley SB-7 (600 lb) or equivalent, 1/16” screen perforation.

Check:	Bronze body, bronze trim, bronze rotating swing disc, threaded ends.

Valves, Larger than 2”:

Pressure Class:	150

End Connection:	Raised Face Flange (ASME B16.5)

Material:	A216-WCB Cast Steel

Ball:	Standard port, 316 SS ball & stem, 2-1/4” stem extension, Teflon seats. Apollo 88B-140-04-35 Series or equivalent.

Gate:	Bolted bonnet, OS&Y, rising stem, solid wedge with bronze seat rings, flanged ends, class 125 iron body with bronze trim, MSS SP-70. Add valve stem extensions to all valves that will be installed in insulated piping systems.

Butterfly:	Lug-style double-offset high-performance butterfly valve for double dead-end service; carbon steel body with stainless stem and disc, RTFE seats. Crane Flowseal xx-1LA-12DPGG, Jamesbury 815L, Pratt HP2-150-xxx-663G, DeZURIK BHP L1 or equivalent.

Check:	Bolted bonnet, API Trim 8. Crane 147XUF, Powell 1561FC8G, Velan F-2014C-02TY or equivalent.

Non-Slam Check:	Carbon steel body, double-flanged retainerless spring-loaded check valve, EPDM seat (No Buna-N).

Expansion Joints:	EPDM Tube with EPDM cover. Primed and painted carbon steel split retainer ring. Where required, control rods, gussets, and compressions sleeves shall be stainless steel.

Special Notes:	No Buna-N materials. Marine coating required for exterior or flooded service.